## Instructions
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Instructions
Version Number: | 1
Latest Revision Date: | 2012-10-01
Reference Test Procedure
10 CFR 431.106: Uniform Test Method for Measuring the Energy Efficiency of Commercial Water Heaters [77 FR 28928, May 16, 2012]
Table of Contents
Tab | Contents
Instructions | Instructions and table of contents
General Info & Test Results | Lab information, product information, and test results
Setup & Instrumentation | Instrumentation used to conduct test measurements
Storage Tank Volume | Storage tank volume measurement inputs and calculations
Test Conditions | Table of test condition requirements for each test
Thermal Efficiency Test | Thermal efficiency test measurement inputs and calculations
Standby Loss Test | Standby loss test measurement inputs and calculations
Photos | Photographs taken during test
Comments | Inputs for report template user to provide comments
Report Sign-Off Block | Report review history
Drop-Downs | Used for drop-down lists; summary of drop-down options
Version Control | Report template revision history
LEGEND
Blue tabs have cells requiring inputs
Input cell
Provided Data
Calculated Value (auto-filled)
NOT USED
Instructions for Completing this Template
Follow the steps below, filling in all input cells (shaded light blue) in each tab you are instructed to complete. Using TAB to "hop" from input cell to input cell is useful, but does not ensure that all input cells are reached. To guarantee that you enter all required information, you must visually scan for light blue cells in the entire area bounded by yellow-shaded cells.
Important: Start with a clean (unused) template copy for each new report. Enter only data and information that are unique to the unit tested and the current test of that unit. All abbreviations and variable names should be consistent with the reference test procedure.
STEP: | FILL IN INPUT CELLS IN THE CORRESPONDING TAB:
Before Test Set-up and Before Start of Test
Step 1 | General Info & Test Results
After Test Set-up and Before Start of Test
Step 2 | Setup & Instrumentation
After Completion of the Test
Step 3 | Storage Tank Volume
Step 4 | Test Conditions
Step 5 | Thermal Efficiency Test
Step 6 | Standby Loss Test
Step 7 | Photos, if applicable
Step 8 | Comments
Determine Test Results
Step 9 | Report Sign-Off Block

## General Info & Test Results
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | General Info & Test Results
Version Number: | 1 | Back to Instructions tab
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Lab Information |  | Figures of Merit for Tested Unit
Lab Name: | [Lab Name] | Variable | Measurement | Units
Lab Location: | [Location of Lab] | Storage Capacity, Va | 0 | gal
|  | Thermal Efficiency, Et | #DIV/0! | %
Test Information |  | Standby Losses | #DIV/0! | Btu/hr
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
Are Photos needed for this test?
NOTE: Copy only; sign off is done in the Report Sign-Off Block tab
Product Information |  | Test Report Sign-Off Block
Brand: |  | We certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Manufacturer :
Manufacturer Model Number:
Serial Number: |  | Role |  | Date | Entity
Date Manufactured: |  | Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Type: |  | Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Date Product Received: | [MM/DD/YYYY] | Report Reviewed by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Received by: |  | Report Reviewed by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Condition as Received: |  | Report Reviewed by DOE |  | [MM/DD/YYYY] | DOE

## Setup & Instrumentation
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Setup & Instrumentation |  | Back to Instructions tab
Version Number: | 1
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Setup (this table should include instrumentation, sensors, and all equipment used during testing)
Instrument Type | Brand | Model # | Sensor Location | Accuracy | Date of Last Calibration | Deadline for Next Calibration
Please describe the test setup of the flooring and/or platform below the water heater and the placement of the water heater in the test room.
Please provide the piping insulation thermal resistence and the length from the connection at the water heater. Describe the test setup of the piping insulation, and the temperature and pressure relief valve insulation.
Please describe the test setup of the heat traps, vent pipe, and the inlet and outlet piping arrangements.

## Storage Tank Volume
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Storage Tank Volume
Version Number: | 1 |  | Back to Instructions tab
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Determination of Storage Tank Volume (according to section 2.30)
For a water heater with a storage vessel or any water heater having an input rating of less than 4,000 Btu per hour per gallon of capacity, the storage capacity shall be within ± 5.0 percent of the manufacturer's rated volume.
Test Start Date: | [MM/DD/YYYY]
| Measurement | Units
Tare Weight, Wt |  | lbs
Filled Weight, Wf |  | lbs
Average Water Inlet Temperature [58 ± 2 deg F], Tin |  | °F
Density of Water, ρ | 8.3248 | lbs/gal
Storage Capacity, Va | 0 | gal
Constants used in Calculations
| Constant | Units
Unadjusted Density of Water, ρ | 8.3248 | lbs/gal
Adjusting Coefficient a Water Density | 0.00121 | lbs/gal°F
Adjusting Coefficient b Water Density | 1.8255e-05 | lbs/gal°F^2
Adjusting Coefficient c Water Density | 2.4875e-08 | lbs/gal°F^3

## Test Conditions
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Test Conditions |  | Back to Instructions tab
Version Number: | 1
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Test Conditions
Test Start Date: | [MM/DD/YYYY]
1. Average Room Ambient Temperature (in accordance with item i in section 2.9)
The ambient air temperature of the test room shall be maintained at 75 °F ± 10 °F (24 °C ± 5.5 °C). The room temperature shall not vary more than ± 7 °F (± 4 °C) from the average during the test.
Average Room Amb. Temperature (°F)
Thermal Efficiency Test
Standby Loss Test
| Min | Max
Thermal Efficiency Test
Standby Loss Test
2. Supply Water Temperature (in accordance with item d in section 2.9).
The temperature of the water being supplied to the water heater shall be maintained at 70 °F ± 2 °F (21 °C ± 1 °C) during the conduct of this test.
Supply Water Temperature (°F)
| Min | Max
Thermal Efficiency Test
Standby Loss Test
3. Supply Water Pressure (in accordance with item d in section 2.9).
During the test when water is not being withdrawn, the supply pressure shall be maintained between 40 psi (275.8 kPa) and the maximum allowable pressure specified by the water heater manufacturer.The accuracy of the pressure measuring devices shall be ±1.0 psi.
Supply Water Pressure (psi)
| Min | Max
Thermal Efficiency Test
Standby Loss Test
4. Gas Outlet Pressure (in accordance with item e in section 2.9).
The outlet pressure of the gas appliance pressure regulator shall be within ±10 percent of that recommended by the manufacturer. For all tests, obtain the higher heating value of the gas burned.
Outlet Gas Pressure (inH2O)
| Min | Max
Thermal Efficiency Test
Standby Loss Test
5. Gas Supply (in accordance with item e in section 2.9, and section 2.3.3 and 2.3.4).
The burners shall be adjusted to their Btu ratingsat normal inlet test pressure. They shall be adjusted so they will be at the manufacturer's hourly Btu rating (±2 percent) 15 minutes after being placed in operation from a room temperature start. The manifold pressure shall be within 10 percent of its rating. Primary air shall be set to give a good flame.
Input Rate (Btu/h)
| Min | Max
Thermal Efficiency Test
6. Setting Tank Thermostat (according to item g in section 2.9)
Before starting testing of a tank-type water heater, the setting of the thermostat shall be obtained starting with the water in the system at 70 ± 2 °F and noting the max mean temperature of the water after the themostat reduces the gas supply to a minimum. The temperature shall be 140 ± 5°F.
Maximum Mean Water Temperature After Thermostat Reduces Gas Supply to a Minimum |  | °F

## Thermal Efficiency Test
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Thermal Efficiency Test
Version Number: | 1 |  | Back to Instructions tab
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Efficiency Measurement in Active Mode (according to item j in section 2.9) | [5 empty] | Constants used in Efficiency Measurement
The outlet water temperature shall be adjusted by varying the rate of flow until the temperature is constant at 70 °F± 2 °F above the supply temperature. After the outlet temperature is constant, as indicated by no variation in excess of 2 °F over a 3 minute period, the outlet water shall be diverted from the waste line to the weighing container. Water shall flow for exactly 30 minutes, at which the total gas and electrical power consumption shall be measured as well as the weight of the water in the container. | [6 empty] | Constant | Units
Test Start Date: | [MM/DD/YYYY] |  |  |  |  | Nominal Specific Heat of Water at 105 °F | 1.004 | [Btu/lb°F]
Thermal Efficiency, Et (percent) | #DIV/0!
Total Weight of Water Heated (lbs) |  | After flowing into weighing container for exactly 30 minutes, or measured by a water meter.
Metered Gas Consumed (ft3) |  | Of the factory supplied heater components and of the test loop-recirculating pump, if used.
Measured Electricity Consumed (kWh) |  | Of the factory supplied heater components and of the test loop-recirculating pump, if used.
Heating Value of Gas (Btu/ft3 @ 60 °F, 30 in. Hg, saturated)
Meter Correction Factor (saturated to dry)
Average Atmospheric Pressure (in. Hg)
Average Gas Supply Pressure (in. WC)
Average Gas Supply Temperature (°F)
Average T1 (supply water, °F) | #DIV/0!
Average T2 (outlet water, °F) | #DIV/0!
Specific Heat of Water Drawn, Cpi (Btu/lb-°F) | #DIV/0!
Temperature Rise (°F) | #DIV/0!
HHV (Btu/ft3 @ 60 °F, 30 in. Hg, dry) | 0
Corrected Gas Used ft3 @ 60 °F, 30 in. Hg, dry) | 0
Gas Consumption (Btu) | 0
Electrical Consumption (Btu) | 0
Total BTU | 0
Average room ambient air temperature (°F) | #DIV/0!
Temperature Data |  |  |  | Room Ambient Air Temperature Data
During the conduct of the test, the temperature of the supply water should be maintained at 70 ± 2°F according to item d and j in section 2.9. The timing of this portion shall begin once the outlet temperature has become constant, as indicated by no variation in excess of 2 °F (1°C) over a 3 minute period. |  |  |  | During the conduct of the test, the ambient air temperature shall be maintained at 75 ± 10 °F (24 ± 5.5 °C).
Time, τ | T1 (Supply Water) | T2 (Outlet Water) |  | Time, τ | Tamb
minutes | °F | °F |  | minutes | °F
1 |  |  |  | 0
2 |  |  |  | 15
3 |  |  |  | 30
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30

## Standby Loss Test
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Standby Loss Test |  | Back to Instructions tab
Version Number: | 1
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Standby Loss Test (according to section 2.10)
Test Start Date: | [MM/DD/YYYY]
Efficiency Measurement (according to item j in section 2.9)
Thermal Efficiency, Et (percent) | #DIV/0!
Begin Standby Test (according to section 2.10)
The gas to the main burner(s) shall be turned on and the appliance put into operation. After the first cutout, allow the water heater to remain in the standby mode until the next cutout. At this time, record the time, ambient temperature, and the maximum mean tank temperature.
After the Second Cutout
Time (mins)
Ambient Temperature (°F)
Maximum Mean Tank Temperature (°F)
Standby Heat Loss Measurement (according to section 2.10) |  |  | Constants used in Standby Heat Loss Measurement
Immediately after the conclusion of the test, record the total fuel flow and electrical energy consumption, the final ambientair temperature, the time duration of the standby loss test in hours, and the maximum mean tank temperature that occurs after cutout. |  |  |  | Constant | Units
| Immediately After Test |  | Nominal Specific Heat of Water | 8.25 | [Btu/gallon°F]
Elapsed Time of Standby Loss Test (hours)
Final Mean Tank Temperature (°F)
Total Fuel Flow as Metered (ft3)
Uncorrected HV (Btu/ft3 @ 60 °F, 30 in. Hg, saturated)
Meter Correction Factor (saturated to dry)
HHV (Btu/ft3 @ 60 °F, 30 in. Hg, dry) | 0
Final Ambient Air Temperature (°F)
Max Mean Tank Temp (°F)
Average Atmospheric Pressure (in. Hg)
Average Gas Supply Pressure (in. WC)
Average Gas Supply Temperature (°F)
Corrected Gas Used (ft3 @ 60 °F, 30 in. Hg, dry) | 0
Electrical Energy Consumption (kWh)
Converted Electrical Energy Consumption (Btu) | 0
Density of Stored Hot Water, ρ (lbs/gal) | 8.3248
Cp (BTU/lb °F) | 1.016
Average Mean Tank Temperature (°F) | #DIV/0!
Average Ambient Air Temperature (°F) | #DIV/0!
∆T3 (°F) | #DIV/0!
∆T4 (°F) | 0
Standby Loss, S (percent per hour) | #DIV/0!
Hourly Standby Losses, Qhr (BTU/hr) | #DIV/0!
Standby Loss Measurement Temperature Data
Record the mean tank and ambient air temperature every 15 minutes until the first cutout after 24 hours, or until 48 hours if the water heater is not in heating mode at that time.
Time (min) | Mean Tank Temperature (°F) | Ambient Temperature (°F)
0
15
30
45
60
75
90
105
120
135
150
165
180
195
210
225
240
255
270
285
300
315
330
345
360
375
390
405
420
435
450
465
480
495
510
525
540
555
570
585
600
615
630
645
660
675
690
705
720
735
750
765
780
795
810
825
840
855
870
885
900
915
930
945
960
975
990
1005
1020
1035
1050
1065
1080
1095
1110
1125
1140
1155
1170
1185
1200
1215
1230
1245
1260
1275
1290
1305
1320
1335
1350
1365
1380
1395
1410
1425
1440
1455
1470
1485
1500
1515
1530
1545
1560
1575
1590
1605
1620
1635
1650
1665
1680
1695
1710
1725
1740
1755
1770
1785
1800
1815
1830
1845
1860
1875
1890
1905
1920
1935
1950
1965
1980
1995
2010
2025
2040
2055
2070
2085
2100
2115
2130
2145
2160
2175
2190
2205
2220
2235
2250
2265
2280
2295
2310
2325
2340
2355
2370
2385
2400
2415
2430
2445
2460
2475
2490
2505
2520
2535
2550
2565
2580
2595
2610
2625
2640
2655
2670
2685
2700
2715
2730
2745
2760
2775
2790
2805
2820
2835
2850
2865
2880

## Photos
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Photos | Back to Instructions tab
Version Number: | 1
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
1. Namplate showing model number and serial number. |  |  | 2. FTC EnergyGuide label (if present)
3. ENERGY-STAR Sticker or label if not part of EnergyGuide label (if applicable) |  |  | 4. Overall view of unit installed
5. User-operable controls |  |  | 6. Exact placement of all visible sensors on, in, or around the device
7. View of test set-up: water inlet and outlet plumbing (including thermocouples and any insulation), water heater, and vent pipes |  |  | 8. Additional photos (if necessary)

## Comments
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Comments | Back to Instructions tab
Version Number: | 1
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Comments

## Report Sign-Off Block
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Report Sign-Off Block |  | Back to Instructions tab
Version Number: | 1
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Test Report Sign-Off Block
By signing in the space below, we certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Role |  | Date | Entity
Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Report Reviewed by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Reviewed by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Reviewed by DOE |  | [MM/DD/YYYY] | DOE

## Drop-Downs
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Drop-Downs
Version Number: | 1
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Type |  | Yes_No
Electric Storage |  | Yes
Gas-Fired Storage |  | No
Oil-Fired Storage
Gas-Fired Instantaneous
Hot Water Supply Boilers
Oil-Fired Instantaneous

## Version Control
Title Block
File Name: | Commercial Water Heater - v1.0.xlsx
Tab Name: | Version Control
Version Number: | 1
Latest Revision Date: | 2012-10-01
Test Completion Date: | [MM/DD/YYYY]
Revisions List
Version | Date
0.1 | 2012-08-30
0.2 | 2012-08-30
0.3 | 2012-08-31
0.4 | 2012-09-14
0.5 | 2012-09-17
0.6 | 2012-09-18
0.7 | 2012-09-21
1 | 2012-10-01