## Introduction + Description
FEMP New Technologies Matrix 2010
Workbook
Introduction
The intent of this New Technologies Matrix is to identify and rank emerging and recent technologies which hold the most promise to impact the federal market in order to prioritize resources in the next several years. Therefore these technologies are being selected on the basis that they will be deployable in the short term and have high potential to be incorporated into agency energy-use reduction programs. Technologies were selected through a comprehensive survey of emerging technology evaluation and deployment programs by federal agencies, state energy programs, and public utilities.
This New Technology Matrix Workbook
This workbook contains the top 50 ranked new technologies. The goal of this Matrix is to bring attention to technologies that are new or underused. The Matrix is a high level comparison and it is understood that energy savings and costs will vary significantly with region, climate, and energy prices. The technologies herein should be further evaluated for inclusion in energy improvement projects. Some measures are only cost effective if implemented at the time of new construction or major renovation. Since most measures will take place in existing buildings, retrofitting is the focus of the New Technology Matrix.
Tab Descriptions
Summary - This is a brief listing of the top ranked technologies with break outs for the Top 20 (Table 1), Second Tier Technologies from the remaining set of 30 (Table 2), and the complete listing of technologies ranked from 21 - 50 (Table 3).
Overall Ranking - This list includes all 50 Technologies in ranked order with descriptions and a more detailed break out of scoring.
Tech by Category - Technologies are listed by their major energy end-use category
General Info - This tab provides additional guidance information such as target applications, key factors to consider and points of contact for experts.
Resources - Listings of manufacturers; and links to technology briefs, case studies, reports and available calculators and tools.
Ranking Criteria - More detail on the methodology and how technologies were ranked and scored.
Ranking
Ranking hinges on three major attributes that are each derived from specific capabilities and qualities of that technology in the federal marketplace. Each attribute described below is weighted and scored individually. The ultimate ranking score is a summation of scores and weightings of each attribute. The attributes are:
| 1) | Federal Impact (50% Weighting)– a combination of a technology’s energy savings potential and degree of applicability in the overall federal market. This criterion is scored by the energy savings in terms of percent of total federal energy use. The energy saving percent ranges from near zero to over 2.5%.
| 2) | Cost Effectiveness (30% Weighting)– relative cost of the implementation and average expected return typically reported in case studies as simple payback period. New technology paybacks ranged from below 3 to over 12 years.
| 3) | Probability of Success (20% Weighting) – a combination of characteristics that are mostly qualitative. Each is scored separately with the average being the overall score for “Probability of Success”. The characteristics include:
|  | a. | Strength of Supply Chain – including number manufacturers, maturity of the distribution channel, warranties, and service availability.
|  | b. | Knowledge Base – availability of case studies, design guides and independent evaluations/assessments.
|  | c. | Implementation Difficulty – ease of retrofit, disruption to operations or occupants, and degree of maintenance required.
|  | d. | Customer Acceptance (referring to both the facility operator and occupants) – potential to help meet energy goals, to improve quality of facility and improved aesthetics, for occupant complaints, and for demonstrated history of success.

## Summary
FEMP - New Technologies - Top 20
Table 1
|  | Rank | Technology | Category | Weighted Score
|  | 1 | Spectrally Enhanced Lighting | Lighting | 91
|  | 2 | Low Ambient / Task Lighting | Lighting | 88
|  | 3 | Condensing Boilers | HVAC | 86
|  | 4 | Super T8 Lighting | Lighting | 79
|  | 5 | Commercial Ground-source Heat Pumps | HVAC | 66
|  | 6 | High R-Value Windows | Building Envelope | 65
|  | 7 | Duct Sealants | HVAC | 63
|  | 8 | LED / Solid State Lighting - Interior | Lighting | 61
|  | 9 | LED / Solid State Lighting - Exterior | Lighting | 59
|  | 10 | PC Power Management | Other | 58
|  | 11 | Condensing Water Heaters - gas | Water Heating | 58
|  | 12 | Water Cooled Oil Free Magnetic Bearing Compressor | HVAC | 54
|  | 13 | Integrated Daylighting Systems | Lighting | 53
|  | 14 | Cool Roofs | Building Envelope | 53
|  | 15 | Bi-level Garage / Parking Lot / Pedestrian Lighting | Lighting | 53
|  | 16 | Wrap Around Heat Pipes | HVAC | 53
|  | 17 | Window Films | Building Envelope | 53
|  | 18 | Commercial Energy Recovery Ventilation Systems (ERV) | HVAC | 52
|  | 19 | Air-side Economizers and Filters for Data Centers | HVAC | 52
|  | 20 | Induction Lighting | Lighting | 51
New Technologies - Second Tier
In reviewing the next 30 technologies in the ranking (see Table 3 below for complete list) a small group is considered worth pursuing for application to federal government facilities. These technologies should have significant impact in saving energy and have potential for broad scale adoption. These technologies are grouped by the categories presented below.
Table 2
|  | Rank | Technology | Category | Weighted Score
Dry Climate Technologies
|  | 32 | Multi-Stage Indirect Evaporative Cooling | HVAC | 48
|  | 44 | Evaporative Precooling Systems | HVAC | 36
Humid Climate Technologies
|  | 34 | Dehumidification Enhancements for A/C in hot-humid climates | HVAC | 46
|  | 38 | Liquid Desiccant Air Conditioner | HVAC | 42
Hi-Bay Lighting Technologies
|  | 21 | HID Electronic/Dimming Ballasts | Lighting | 51
|  | 36 | Efficient High Bay Fluorescent Lighting | Lighting | 42
|  | 42 | High Bay LED | Lighting | 37
HVAC Control Retrofits
|  | 22 | HVAC Occupancy Sensors | HVAC | 51
|  | 27 | CO2 Demand Ventilation Control (DVC) | HVAC | 50
|  | 29 | Demand Control Ventilation for Commercial Kitchen Hoods | HVAC | 50
|  | 35 | Compressor Cycling Controller | HVAC | 45
Other Important Technologies
|  | 24 | Data Center Cooling System Air Distribution Optimization | HVAC | 51
|  | 37 | Advanced Rooftop Packaged AC | HVAC | 42
|  | 26 | Bi Level Stairwell Lighting | Lighting | 50
New Technologies Ranked 21 - 50
Table 3
|  | Rank | Technology | Category | Weighted Score
|  | 21 | HID Electronic/Dimming Ballasts | Lighting | 51
|  | 22 | HVAC Occupancy Sensors | HVAC | 51
|  | 23 | Vending Machine Occupancy Sensor | Other | 51
|  | 24 | Data Center Cooling System Air Distribution Optimization | HVAC | 51
|  | 25 | Tankless Water Heater - Gas | Water heating | 50
|  | 26 | Bi Level Stairwell Lighting | Lighting | 50
|  | 27 | CO2 Demand Ventilation Control (DVC) | HVAC | 50
|  | 28 | Thermal Displacement Ventilation | HVAC | 50
|  | 29 | Demand Control Ventilation for Commercial Kitchen Hoods | HVAC | 50
|  | 30 | Active Chilled Beam Cooling with Dedicated OSA Ventilation | HVAC | 49
|  | 31 | Heat Pump Water Heater | Water Heating | 48
|  | 32 | Multi-Stage Indirect Evaporative Cooling | HVAC | 48
|  | 33 | Colored Paint for heat reflective or absorptive applications | Building Envelope | 47
|  | 34 | Dehumidification Enhancements for A/C in hot-humid climates | HVAC | 46
|  | 35 | Compressor Cycling Controller | HVAC | 45
|  | 36 | Efficient High Bay Fluorescent Lighting | Lighting | 42
|  | 37 | Advanced Rooftop Packaged AC | HVAC | 42
|  | 38 | Liquid Desiccant Air Conditioner | HVAC | 42
|  | 39 | Solar Water Heating | Water Heating | 41
|  | 40 | Thermal Destratifiers | HVAC | 40
|  | 41 | Refrigeration Management System | Refrigeration | 38
|  | 42 | High Bay LED | Lighting | 37
|  | 43 | Off-peak Precooling | HVAC | 37
|  | 44 | Evaporative Precooling Systems | HVAC | 36
|  | 45 | Wireless Temperature Sensors | HVAC | 34
|  | 46 | Airfield LED Lighting | Lighting | 34
|  | 47 | Green Roofs | Building Envelope | 33
|  | 48 | Aerogel Insulation - Piping, Ducts, and Buildings | Building Envelope | 28
|  | 49 | Smart Windows | Building Envelope | 25
|  | 50 | Phase Change Insulation | Building Envelope | 21

## Overall Ranking
FEMP - New Technologies - Overall Ranking for the Federal Sector
| * See Ranking Criteria Tab |  |  | Scale: 5 = Highest , 0 = Lowest
Ranking Criteria *
Rank | Technology | Category | Description | Overall Federal Building Energy Savings | Cost Effectiveness | Probability of Success | Weighted Score
(1-100)
1 | Spectrally Enhanced Lighting | Lighting | DOE research studies show that by simply shifting the color in fluorescent lamps from the warmer yellow to the cooler blue end of the color spectrum, people see things more clearly and spaces appear brighter. Therefore, by changing the color of light to be more like daylight, lighting levels can be reduced to save energy while still achieving the same visual acuity. Conventional practice utilizes lamps with correlated color temperature (CCT) of 3000K to 4100K and SEL uses lamps with a CCT of 5000K. In T8s with electronically ballasted fluorescent lighting systems, this translates to a 20 percent energy savings, and in T12s with magnetically ballasted systems, SEL can achieve a 50 percent savings. | 4.9 | 4 | 4.5 | 91
2 | Low Ambient / Task Lighting | Lighting | The low ambient / task strategy improves the visual environment by adding controllable task fixtures that provide light directly where its needed for a given task, while reducing the overhead (ambient) light level. Occupancy sensors can also be incorporated into the system. | 5 | 4 | 3.5 | 88
3 | Condensing Boilers | HVAC | Commercial boilers that are high efficiency due to their design to extract heat from flue gas moisture | 5 | 3 | 4.5 | 86
4 | Super T8 Lighting | Lighting | Super T8 lamps are 32W T8 lamps but with a barrier-coat design, high lumen maintenance (88-92 percent end-of-life lumens), long service life and high light output—3100+ initial lumens as opposed to 2850 for a standard T8. Combining Super T8 Lamps with low ballast factor ballasts (BF of ≤ 0.77) on a one-for-one replacement will save 15 to 20%. | 3.5 | 4 | 5 | 79
5 | Commercial ground source heat pumps | HVAC | A ground source heat pump with loops feeding multiple packaged heat pumps and having a single ground source water loop. Unit capacity is typically 1-10 tons and may be utilized in an array of multiple units to serve a large load. | 2.8 | 4 | 3.5 | 66
6 | High R-Value Windows | Building Envelope | Highly insulating windows triple pane R5 or greater (U value 0.22 and lower) windows | 3.7 | 2 | 4 | 65
7 | Duct Sealants | HVAC | Aerosol sealant is injected into the duct work to seal leaks. Can save on heating, cooling and fan energy, depending on building. | 1.6 | 5 | 4.3 | 63
8 | LED / Solid State Lighting - Interior | Lighting | Interior LED retrofits are currently viable for downlights, track lighting, sconces, and task lighting both line and low voltage. Replacements for incandescent A-Lamps have also been improving rapidly. Replacements for fluorescent tube lighting may be viable for high cost maintenance areas. | 2.5 | 3 | 4.5 | 61
9 | LED / Solid State Lighting - Exterior | Lighting | LED lighting economics can work in high electric cost area with lot of hours of use. Pricing is continually decreasing. Provides quality, white even lighting with good color rendition. When combined with bi-level motion sensors to reduce light levels in parking areas, garages and walk ways, greater cost effective savings can be achieved. | 2.2 | 3 | 4.8 | 59
10 | PC Power Management | Other | Network based software that manages the power consumption of computers by automatically putting them in stand-by or hibernate or other low energy consuming state without interfering with user productivity or IT functions. | 0.8 | 5 | 5 | 58
11 | Condensing Water Heaters - Gas | Water Heating | Gas water heater that condenses water out of the flue gas to achieve higher efficiencies | 0.8 | 5 | 5 | 58
12 | Water Cooled Oil Free Magnetic Bearing Compressors | HVAC | Magnetic bearing, oil free 60 to 80 ton chiller compressor (also 150 tons). Onboard VFD and micro processor. Also small, light, quiet, low startup draw. | 1 | 4 | 5 | 54
13 | Integrated Day lighting Systems | Lighting | Add electronic dimmable fluorescent ballasts, photosensors, and occupancy sensors where appropriate. This can be combined with network components, workstation controls and building management options. Integrated controls will provide significant savings on applied systems. | 2 | 3 | 3.8 | 53
14 | Cool Roofs | Building Envelope | Cool roofs—roofs that stay cool in the sun by minimizing solar absorption and maximizing thermal emission—lessen the flow of heat from the roof into the building, reducing the need for space cooling energy in conditioned buildings. Cool roofs may also increase the need for heating energy in cold climates. For a commercial building, the decrease in annual cooling load is typically much greater than the increase in annual heating load. | 1 | 4 | 4.8 | 53
15 | Bi Level Garage / Parking Lot / Pedestrian Lighting | Lighting | This technology uses fluorescent and LED lighting sources with bi-level motion sensors to reduce lighting levels when the parking area is not in use. This technology can also be applied to pathway lighting where appropriate. | 0.9 | 4 | 5 | 53
16 | Wrap Around Heat Pipes | HVAC | Where humidity control is critical the typical way to do it is to over cool the air to condense out the excess moisture. Air is then too cold to supply to the space so the air must be reheated. Wrap around heat pipes wrap around the cooling coil to pre-cool the outside air before it hits the cooling coil allowing the cooling coil to do more work condensing out moisture. The heat pipe then re-heats the air on the backside of the cooling coil so it doesn’t have to be re-heated with strip heaters or some other means. | 0.5 | 5 | 4.5 | 53
17 | Window Films | Building Envelope | A spectrally selective film used to decrease heat gained through a window | 0.3 | 5 | 5 | 53
18 | Commercial Energy Recovery Ventilation Systems (ERV) | HVAC | ERV systems exchange heat between the outgoing exhaust air and the ventilation air being brought in. This allows reducing the capacity of the HVAC system and saves energy. Heat and energy recovery wheels are the most common. Other types include: energy recovery loops, heat pipes, plate exchangers. Some transfer both sensible and latent heat. | 0.9 | 4 | 4.8 | 52
19 | Air-side Economizers and Filters for Data Centers | HVAC | Install 100% outside-air cooling capability in a data center to provide free cooling. | 0.2 | 5 | 5 | 52
20 | Induction Lighting | Lighting | Induction lighting is essentially a fluorescent light without electrodes or filaments, the items that frequently cause other bulbs to burn out quickly. Induction lamps offer the potential for very long life—up to 100,000 hours—while providing good color quality at competitive efficiencies. | 1.5 | 3 | 4.5 | 51
21 | HID Electronic/Dimming Ballasts | Lighting | Most of these lights, typically metal halide or high pressure sodium lamps, are currently driven by magnetic ballasts. Several manufacturers now offer electronic ballasts (EBs) for these lamps. EBs promise better efficiency, longer lamp life, and faster start-up and restrike. | 1.3 | 4 | 3.5 | 51
22 | HVAC Occupancy Sensors | HVAC | Uses an occupancy sensor to detect when people are in spaces. When no one is in the room, controls reduce the thermostat setpoint in the winter and raise it in the summer. | 0.6 | 5 | 3.8 | 51
23 | Vending Machine Occupancy Sensor | Other | Device detects when there are no personnel in the vicinity and powers down beverage vending machines. Does not completely turn off compressor, but reduces run times. | 0.1 | 5 | 5 | 51
24 | Data Center Cooling System Air Distribution Optimization | HVAC | Implement appropriate air distribution controls to prevent the mixing and recirculation of data center air before it reaches the servers. This is done by confining the chilled air distribution to data center cold aisles. | 0.1 | 5 | 5 | 51
25 | Tankless Water Heater - Gas | Water heating | Water heater that does not have a storage tank. Sold in condensing and non-condensing. A conventional non-condensing storage tank water heater has an EF of 0.60 and a typical non-condensing tankless water heater has an EF of 0.80. Efficiencies are dependent on the frequency of water draws for tankless WHs and total hot water consumption for tank type WHs. | 0.9 | 4 | 4.3 | 50
26 | Bi Level Stairwell Lighting | Lighting | These products use integral occupancy sensor motion detectors to monitor the stairwell. When occupancy is detected, the lights go to full level. When the space has been vacated after a programmed period of time, the fixture goes to a minimum level. | 0.6 | 4 | 5 | 50
27 | CO2 Demand Ventilation Control (DVC) | HVAC | A DVC system modulates the level of ventilation to a building based on the current occupancy of the building, saving energy while still maintaining proper IAQ. Carbon dioxide sensors are commonly used but a multiple-parameter approach using TVOC, PM, formaldehyde an RH levels can also be used.CO2 sensors control the outside air damper to reduce the amount of outside air that needs to be conditioned and supplied to the building when occupancy is low. Works especially well for conference rooms and auditoriums that are frequently low occupancy but must be designed to supply outside air volume for worst case scenario. | 0.5 | 5 | 3.8 | 50
28 | Thermal Displacement Ventilation | HVAC | Thermal displacement ventilation provides slightly cooled air into the space at relatively low velocity, either through a raised floor system or via wall diffusers near floor level. These are combined with a 100% outside air system and can also provide heating. | 0.3 | 5 | 4.3 | 50
29 | Demand Control Ventilation for Commercial Kitchen Hoods | HVAC | A demand control ventilation system (DCV) is an energy management system for commercial kitchen hoods. It optimizes energy efficiency by reducing the exhaust and MUA fan speed. This is accomplished by leveraging sensors to determine the minimum amount of exhaust air required to capture and contain effluent from the cook line. | 0.1 | 5 | 4.8 | 50
30 | Active Chilled Beam Cooling with Dedicated OSA Ventilation | HVAC | In a "chilled beam" system chiller energy is delivered efficiently to the zone by being carried in water. Air in occupied spaces is passed across the radiant chilled beam. Warmer water is used than in a VAV system, which helps reduces energy consumption. Small amounts of outdoor air are entrained into the larger supply of recirculated air to provide required ratio of fresh air. | 0.3 | 5 | 4 | 49
31 | Heat Pump Water Heater | Water Heating | Air to water heat pump to replace an electric resistance water heater. | 0.7 | 4 | 4.3 | 48
32 | Multi-Stage Indirect Evaporative Cooling | HVAC | An advanced evaporative cooler that can lower air temperatures without adding moisture. These systems evaporate water in a secondary (or working) airstream, which is discharged in multiple stages. No water or humidity is added to the primary (or product) airstream in the process. | 0.6 | 5 | 3 | 48
33 | Colored Paint for Heat Reflective or Absorptive Applications | Building Envelope | New technology allows for paint to be any color in the visible spectrum, yet have either absorptive or reflective properties in the heat spectrum. | 0.1 | 5 | 4 | 47
34 | Dehumidification Enhancements for Air Conditioning in Hot-Humid Climates | HVAC | Incorporation of a Cromer cycle dehumidification feature on a packaged air conditioner in hot-humid climates. The Cromer cycle is a novel combination of a desiccant wheel and a vapor compression air conditioner. | 0.5 | 5 | 2.8 | 46
35 | Compressor Cycling Controller | HVAC | Add-on system compliments existing controls to maximize (optimize) compressor operation. Software dynamically analyzes compressor cycles, achieving an overall reduction in run time without causing over cycling. Energy efficiency gains are achieved without affecting cooling capacity | 0.4 | 5 | 2.8 | 45
36 | Efficient High Bay Fluorescent Lighting | Lighting | These can include either T5 or T8 fluorescent lighting systems for high-bay applications currently using metal halide fixtures. Fluorescent fixtures offer better light distribution, better light maintenance over the life of the lamp, improved color quality and on-off control (re-strike time) with lower energy consumption. | 1.2 | 2 | 4.5 | 42
37 | Advanced Rooftop Packaged AC | HVAC | Roof top AC with features that can improve their efficiency. These include Improved fans, economizers, diagnostics. Roof top units that have (a) condensing units that drain to the interior of a building, (b) better insulation, (3) duct dampers that prevent off-cycle losses due to convection loops that loose heat from the building. In addition, a roof top unit with a modulating compressor will be more efficient and have better humidity control (if the indoor blower or air handler is also variable speed). | 0.6 | 3 | 4.4 | 42
38 | Liquid Desiccant Air Conditioner | HVAC | A liquid desiccant air conditioner (LDAC) deeply dries air using natural gas, solar energy, waste heat, bio-fuel or other fossil fuel to drive the system. By providing mostly latent cooling, the LDAC controls indoor humidity without overcooling and reheating. This unit is supplemented by an electric chiller or DX air conditioner that sensibly cools the building's recirculation air. The liquid desiccant is a concentrated salt solution that directly absorbs moisture. Most attractive in humid climates. | 0.5 | 4 | 3.3 | 42
39 | Solar Water Heating | Water Heating | Using solar thermal collectors to heat water for commercial building hot water | 0.6 | 3 | 4.3 | 41
40 | Thermal Destratifiers | HVAC | Small turbine like fans are mounted near the ceiling in high bay buildings such as hangars and warehouses to move warm air down to the occupant level in the heating season resulting in using less energy to heat the building. Needs to be installed in well insulated high bay buildings. | 0.2 | 4 | 3.5 | 40
41 | Refrigeration Management System | Refrigeration | Refrigeration Management System for walk-in coolers and freezers | 0.2 | 4 | 3 | 38
42 | High Bay LED | Lighting | LED light sources offer several potential benefits compared to metal halide or fluorescent: reduced energy consumption because of the ability to provide a more precise light distribution; longer operating life and lower maintenance requirements; less heat introduced into the space; and greater controllability for dimming and on/off control. The net result is an overall potential for life cycle savings despite the current high cost of the technology. Relevant to the cold storage application, LED performance improves in colder temperatures. | 1.6 | 1 | 3.8 | 37
43 | Off-peak Precooling | HVAC | Air conditioning and associated ventilation accounts for almost half of peak electric demand of commercial buildings so using off-peak electricity to provide a significant portion of space cooling can achieve considerable electricity cost savings. | 0.1 | 4 | 3 | 37
44 | Evaporative Precooling Systems | HVAC | Evaporative Precooling System installs ahead of the condenser to lower the condenser pressure. These systems can also work with an economizer. Overall evaporative precooling reduces the requirement for energy intensive DX cooling. | 0.3 | 3 | 3.8 | 36
45 | Wireless Temperature Sensors | HVAC | Wireless thermostats are connected into a building automation system (BAS). Ease of adding temperature sensors in more zones allows for greater spatial resolution of zone temperatures thereby providing confidence in control improvements through thermostat reset. In addition, ease of moving thermostats allows for a diagnostic capability in checking existing hard-wired thermostats. | 0.1 | 4 | 2.3 | 34
46 | Airfield LED Lighting | Lighting | Good application for colored LED lights, since LED is monochromatic. Reduced maintenance costs dramatically improve economics over existing incandescent. | 0.1 | 3 | 3.8 | 34
47 | Green Roofs | Building Envelope | Vegetation on the roof reduces heat load and adds insulation to the roof. Reduces storm runoff from roof. | 0.4 | 3 | 2.8 | 33
48 | Aerogel Insulation - Piping, Ducts, and Buildings | Building Envelope | Aerogel products displace current insulation material. As the thermal conductivity of the aerogels is so low, aerogel insulation tends to be far thinner than current insulation. | 0.2 | 3 | 2 | 28
49 | Smart Windows | Building Envelope | Electrochromic glass uses electrical energy to transition between clear and darkened states. Darkened glass transmits less light and reduces heat gain when darkened, especially in dual pane windows. | 0.6 | 2 | 1.8 | 25
50 | Phase Change Insulation | Building Envelope | Insulation or drywall that contains phase change material and therefore has a similar effect as increasing thermal mass. | 0.5 | 2 | 1 | 21

## Tech by Category
FEMP - New Technologies for the Federal Buildings - by Category & Rank
* See Ranking Criteria Tab
Scale: 5 = Highest , 0 = Lowest
Lighting |  |  | Ranking Criteria *
Rank | Technology | Description | Overall Federal Building Energy Savings | Cost Effectiveness | Probability of Success | Weighted Score
1 | Spectrally Enhanced Lighting | DOE research studies show that by simply shifting the color in fluorescent lamps from the warmer yellow to the cooler blue end of the color spectrum, people see things more clearly and spaces appear brighter. Therefore, by changing the color of light to be more like daylight, lighting levels can be reduced to save energy while still achieving the same visual acuity. Conventional practice utilizes lamps with correlated color temperature (CCT) of 3000K to 4100K and SEL uses lamps with a CCT of 5000K. In T8s with electronically ballasted fluorescent lighting systems, this translates to a 20 percent energy savings, and in T12s with magnetically ballasted systems, SEL can achieve a 50 percent savings. | 4.9 | 4 | 4.5 | 91
2 | Low Ambient / Task Lighting | The low ambient / task strategy improves the visual environment by adding controllable task fixtures that provide light directly where its needed for a given task, while reducing the overhead (ambient) light level. Occupancy sensors can also be incorporated into the system. | 5 | 4 | 3.5 | 88
4 | Super T8 Lighting | Super T8 lamps are 32W T8 lamps but with a barrier-coat design, high lumen maintenance (88-92 percent end-of-life lumens), long service life and high light output—3100+ initial lumens as opposed to 2850 for a standard T8. Combining Super T8 Lamps with low ballast factor ballasts (BF of ≤ 0.77) on a one-for-one replacement will save 15 to 20%. | 3.5 | 4 | 5 | 79
8 | LED / Solid State Lighting - Interior | Interior LED retrofits are currently viable for downlights, track lighting, sconces, and task lighting both line and low voltage. Replacements for incandescent A-Lamps have also been improving rapidly. Replacements for fluorescent tube lighting may be viable for high cost maintenance areas. | 2.5 | 3 | 4.5 | 61
9 | LED / Solid State Lighting - Exterior | LED lighting economics can work in high electric cost area with lot of hours of use. Pricing is continually decreasing. Provides quality, white even lighting with good color rendition. When combined with bi-level motion sensors to reduce light levels in parking areas, garages and walk ways, greater cost effective savings can be achieved. | 2.2 | 3 | 4.8 | 59
13 | Integrated Daylighting Systems | Add electronic dimmable fluorescent ballasts, photosensors, and occupancy sensors where appropriate. This can be combined with network components, workstation controls and building management options. Integrated controls will provide significant savings on applied systems. | 2 | 3 | 3.8 | 53
15 | Bi Level LED Garage / Parking Lot / Pedestrian Lighting | This technology uses fluorescent and LED lighting sources with bi-level motion sensors to reduce lighting levels when the parking area is not in use. This technology can also be applied to pathway lighting where appropriate. | 0.9 | 4 | 5 | 53
20 | Induction Lighting | Induction lighting is essentially a fluorescent light without electrodes or filaments, the items that frequently cause other bulbs to burn out quickly. Induction lamps offer the potential for very long life—up to 100,000 hours—while providing good color quality at competitive efficiencies. | 1.5 | 3 | 4.5 | 51
21 | HID Electronic/Dimming Ballasts | Most of these lights, typically metal halide or high pressure sodium lamps, are currently driven by magnetic ballasts. Several manufacturers now offer electronic ballasts (EBs) for these lamps. EBs promise better efficiency, longer lamp life, and faster start-up and restrike. | 1.3 | 4 | 3.5 | 51
26 | Bi Level Stairwell Lighting | These products use integral occupancy sensor motion detectors to monitor the stairwell. When occupancy is detected, the lights go to full level. When the space has been vacated after a programmed period of time, the fixture goes to a minimum level. | 0.6 | 4 | 5 | 50
36 | Efficient High Bay Fluorescent Lighting | These can include either T5 or T8 fluorescent lighting systems for high-bay applications currently using metal halide fixtures. Fluorescent fixtures offer better light distribution, better light maintenance over the life of the lamp, improved color quality and on-off control (re-strike time) with lower energy consumption. | 1.2 | 2 | 4.5 | 42
42 | High Bay LED | LED light sources offer several potential benefits compared to metal halide or fluorescent: reduced energy consumption because of the ability to provide a more precise light distribution; longer operating life and lower maintenance requirements; less heat introduced into the space; and greater controllability for dimming and on/off control. The net result is an overall potential for life cycle savings despite the current high cost of the technology. Relevant to the cold storage application, LED performance improves in colder temperatures. | 1.6 | 1 | 3.8 | 37
46 | Airfield LED Lighting | Good application for colored LED lights, since LED is monochromatic. Reduced maintenance costs dramatically improve economics over existing incandescent. | 0.1 | 3 | 3.8 | 34
HVAC |  |  | Ranking Criteria *
Rank | Technology | Description | Overall Federal Building Energy Savings | Cost Effectiveness | Probability of Success | Weighted Score
3 | Condensing Boilers | Commercial boilers that are high efficiency due to their design to extract heat from flue gas moisture | 5 | 3 | 4.5 | 86
5 | Commercial ground source heat pumps | A ground source heat pump with loops feeding multiple packaged heat pumps and having a single ground source water loop. Unit capacity is typically 1-10 tons and may be utilized in an array of multiple units to serve a large load. | 2.8 | 4 | 3.5 | 66
7 | Duct Sealants | Aerosol sealant is injected into the duct work to seal leaks. Can save on heating, cooling and fan energy, depending on building. | 1.6 | 5 | 4.3 | 63
12 | Water Cooled Oil Free Magnetic Bearing Compressors | Magnetic bearing, oil free 60 to 80 ton chiller compressor (also 150 tons). Onboard VFD and micro processor. Also small, light, quiet, low startup draw. | 1 | 4 | 5 | 54
16 | Wrap Around Heat Pipes | Where humidity control is critical the typical way to do it is to over cool the air to condense out the excess moisture. Air is then too cold to supply to the space so the air must be reheated. Wrap around heat pipes wrap around the cooling coil to pre-cool the outside air before it hits the cooling coil allowing the cooling coil to do more work condensing out moisture. The heat pipe then re-heats the air on the backside of the cooling coil so it doesn’t have to be re-heated with strip heaters or some other means. | 0.5 | 5 | 4.5 | 53
18 | Commercial Energy Recovery Ventilation Systems (ERV) | ERV systems exchange heat between the outgoing exhaust air and the ventilation air being brought in. This allows reducing the capacity of the HVAC system and saves energy. Heat and energy recovery wheels are the most common. Other types include: energy recovery loops, heat pipes, plate exchangers. Some transfer both sensible and latent heat. | 0.9 | 4 | 4.8 | 52
19 | Air-side Economizers and Filters for Data Centers | Install 100% outside-air cooling capability in a data center to provide free cooling. | 0.2 | 5 | 5 | 52
22 | HVAC Occupancy Sensors | Uses an occupancy sensor to detect when people are in spaces. When no one is in the room, controls reduce the thermostat setpoint in the winter and raise it in the summer. | 0.6 | 5 | 3.8 | 51
24 | Data Center Cooling System Air Distribution Optimization | Implement appropriate air distribution controls to prevent the mixing and recirculation of data center air before it reaches the servers. This is done by confining the chilled air distribution to data center cold aisles. | 0.1 | 5 | 5 | 51
27 | CO2 Demand Ventilation Control (DVC) | A DVC system modulates the level of ventilation to a building based on the current occupancy of the building, saving energy while still maintaining proper IAQ. Carbon dioxide sensors are commonly used but a multiple-parameter approach using TVOC, PM, formaldehyde an RH levels can also be used.CO2 sensors control the outside air damper to reduce the amount of outside air that needs to be conditioned and supplied to the building when occupancy is low. Works especially well for conference rooms and auditoriums that are frequently low occupancy but must be designed to supply outside air volume for worst case scenario. | 0.5 | 5 | 3.8 | 50
28 | Thermal Displacement Ventilation | Thermal displacement ventilation provides slightly cooled air into the space at relatively low velocity, either through a raised floor system or via wall diffusers near floor level. These are combined with a 100% outside air system and can also provide heating. | 0.3 | 5 | 4.3 | 50
29 | Demand Control Ventilation for Commercial Kitchen Hoods | A demand control ventilation system (DCV) is an energy management system for commercial kitchen hoods. It optimizes energy efficiency by reducing the exhaust and MUA fan speed. This is accomplished by leveraging sensors to determine the minimum amount of exhaust air required to capture and contain effluent from the cook line. | 0.1 | 5 | 4.8 | 50
30 | Active Chilled Beam Cooling with Dedicated OSA Ventilation | In a "chilled beam" system chiller energy is delivered efficiently to the zone by being carried in water. Air in occupied spaces is passed across the radiant chilled beam. Warmer water is used than in a VAV system, which helps reduces energy consumption. Small amounts of outdoor air are entrained into the larger supply of recirculated air to provide required ratio of fresh air. | 0.3 | 5 | 4 | 49
32 | Multi-Stage Indirect Evaporative Cooling | An advanced evaporative cooler that can lower air temperatures without adding moisture. These systems evaporate water in a secondary (or working) airstream, which is discharged in multiple stages. No water or humidity is added to the primary (or product) airstream in the process. | 0.6 | 5 | 3 | 48
34 | Dehumidification Enhancements for Air Conditioning in Hot-Humid Climates | Incorporation of a Cromer cycle dehumidification feature on a packaged air conditioner in hot-humid climates. The Cromer cycle is a novel combination of a desiccant wheel and a vapor compression air conditioner. | 0.5 | 5 | 2.8 | 46
35 | Compressor Cycling Controller | Add-on system compliments existing controls to maximize (optimize) compressor operation. Software dynamically analyzes compressor cycles, achieving an overall reduction in run time without causing over cycling. Energy efficiency gains are achieved without affecting cooling capacity | 0.4 | 5 | 2.8 | 45
37 | Advanced Rooftop Packaged AC | Roof top AC with features that can improve their efficiency. These include Improved fans, economizers, diagnostics. Roof top units that have (a) condensing units that drain to the interior of a building, (b) better insulation, (3) duct dampers that prevent off-cycle losses due to convection loops that loose heat from the building. In addition, a roof top unit with a modulating compressor will be more efficient and have better humidity control (if the indoor blower or air handler is also variable speed). | 0.6 | 3 | 4.4 | 42
38 | Liquid Desiccant Air Conditioner | A liquid desiccant air conditioner (LDAC) deeply dries air using natural gas, solar energy, waste heat, bio-fuel or other fossil fuel to drive the system. By providing mostly latent cooling, the LDAC controls indoor humidity without overcooling and reheating. This unit is supplemented by an electric chiller or DX air conditioner that sensibly cools the building's recirculation air. The liquid desiccant is a concentrated salt solution that directly absorbs moisture. Most attractive in humid climates. | 0.5 | 4 | 3.3 | 42
40 | Thermal Destratifiers | Small turbine like fans are mounted near the ceiling in high bay buildings such as hangars and warehouses to move warm air down to the occupant level in the heating season resulting in using less energy to heat the building. Needs to be installed in well insulated high bay buildings. | 0.2 | 4 | 3.5 | 40
43 | Off-peak Precooling | Air conditioning and associated ventilation accounts for almost half of peak electric demand of commercial buildings so using off-peak electricity to provide a significant portion of space cooling can achieve considerable electricity cost savings. | 0.1 | 4 | 3 | 37
44 | Evaporative Precooling Systems | Evaporative Precooling System installs ahead of the condenser to lower the condenser pressure. These systems can also work with an economizer. Overall evaporative precooling reduces the requirement for energy intensive DX cooling. | 0.3 | 3 | 3.8 | 36
45 | Wireless Temperature Sensors | Wireless thermostats are connected into a building automation system (BAS). Ease of adding temperature sensors in more zones allows for greater spatial resolution of zone temperatures thereby providing confidence in control improvements through thermostat reset. In addition, ease of moving thermostats allows for a diagnostic capability in checking existing hard-wired thermostats. | 0.1 | 4 | 2.3 | 34
Building Envelope |  |  | Ranking Criteria *
Rank | Technology | Description | Overall Federal Building Energy Savings | Cost Effectiveness | Probability of Success | Weighted Score
6 | High R-Value Windows | Highly insulating windows triple pane R5 or greater (U value 0.22 and lower) windows | 3.7 | 2 | 4 | 65
14 | Cool Roofs | Cool roofs—roofs that stay cool in the sun by minimizing solar absorption and maximizing thermal emission—lessen the flow of heat from the roof into the building, reducing the need for space cooling energy in conditioned buildings. Cool roofs may also increase the need for heating energy in cold climates. For a commercial building, the decrease in annual cooling load is typically much greater than the increase in annual heating load. | 1 | 4 | 4.8 | 53
17 | Window Films | A spectrally selective film used to decrease heat gained through a window | 0.3 | 5 | 5 | 53
33 | Colored Paint for Heat Reflective or Absorptive Applications | New technology allows for paint to be any color in the visible spectrum, yet have either absorptive or reflective properties in the heat spectrum. | 0.1 | 5 | 4 | 47
47 | Green Roofs | Vegetation on the roof reduces heat load and adds insulation to the roof. Reduces storm runoff from roof. | 0.4 | 3 | 2.8 | 33
48 | Aerogel Insulation - Piping, Ducts, and Buildings | Aerogel products displace current insulation material. As the thermal conductivity of the aerogels is so low, aerogel insulation tends to be far thinner than current insulation. | 0.2 | 3 | 2 | 28
49 | Smart Windows | Electrochromic glass uses electrical energy to transition between clear and darkened states. Darkened glass transmits less light and reduces heat gain when darkened, especially in dual pane windows. | 0.6 | 2 | 1.8 | 25
50 | Phase Change Insulation | Insulation or drywall that contains phase change material and therefore has a similar effect as increasing thermal mass. | 0.5 | 2 | 1 | 21
Water Heating |  |  | Ranking Criteria *
Rank | Technology | Description | Overall Federal Building Energy Savings | Cost Effectiveness | Probability of Success | Weighted Score
11 | Condensing Water Heaters - Gas | Gas water heater that condenses water out of the flue gas to achieve higher efficiencies | 0.8 | 5 | 5 | 58
25 | Tankless Water Heater - Gas | Water heater that does not have a storage tank. Sold in condensing and non-condensing. A conventional non-condensing storage tank water heater has an EF of 0.60 and a typical non-condensing tankless water heater has an EF of 0.80. Efficiencies are dependent on the frequency of water draws for tankless WHs and total hot water consumption for tank type WHs. | 0.9 | 4 | 4.3 | 50
31 | Heat Pump Water Heater | Air to water heat pump to replace an electric resistance water heater. | 0.7 | 4 | 4.3 | 48
39 | Solar Water Heating | Using solar thermal collectors to heat water for commercial building hot water | 0.6 | 3 | 4.3 | 41
Refrigeration |  |  | Ranking Criteria *
Rank | Technology | Description | Overall Federal Building Energy Savings | Cost Effectiveness | Probability of Success | Weighted Score
41 | Refrigeration Management System | Refrigeration Management System for walk-in coolers and freezers | 0.2 | 4 | 3 | 38
Other |  |  | Ranking Criteria *
Rank | Technology | Description | Overall Federal Building Energy Savings | Cost Effectiveness | Probability of Success | Weighted Score
10 | PC Power Management | Network based software that manages the power consumption of computers by automatically putting them in stand-by or hibernate or other low energy consuming state without interfering with user productivity or IT functions. | 0.8 | 5 | 5 | 58
23 | Vending Machine Occupancy Sensor | Device detects when there are no personnel in the vicinity and powers down beverage vending machines. Does not completely turn off compressor, but reduces run times. | 0.1 | 5 | 5 | 51

## General Info
FEMP - New Technologies - General Information
Rank | Technology | Application | Description | Key Factors to Consider | Points of Contact
Lighting
1 | Spectrally Enhanced Lighting | Almost any fluorescent lighting system in most building types and settings. | DOE research studies show that by simply shifting the color in fluorescent lamps from the warmer yellow to the cooler blue end of the color spectrum, people see things more clearly and spaces appear brighter. Therefore, by changing the color of light to be more like daylight, lighting levels can be reduced to save energy while still achieving the same visual acuity. Conventional practice utilizes lamps with correlated color temperature (CCT) of 3000K to 4100K and SEL uses lamps with a CCT of 5000K. In T8s with electronically ballasted fluorescent lighting systems, this translates to a 20 percent energy savings, and in T12s with magnetically ballasted systems, SEL can achieve a 50 percent savings. | SEL can be used as a based strategy in combination with other fluorescent lighting based measures such as Low Ambient / Task Lighting, delamping configurations and daylighting controls. To maximize occupant acceptance and comfort, SEL should be done so that color comparison with lower color temperature fluorescent lighting is minimized. | Konstantinos Papamichael, UC Davis & CLTC, 520-747-3834, kpapamichael@ucdavis.edu, Brian Liebel, The Lighting Partnership, (561) 202-1993, brian@thelighting partnership.com Sam Berman, sam.berman@comcast.net; Eric Richman, PNNL, eric.richman@pnl.gov
2 | Low Ambient / Task Lighting | Suitable for most office spaces, both cubicle and private office space environments, in most building categories. | The low ambient / task strategy improves the visual environment by adding controllable task fixtures that provide light directly where its needed for a given task, while reducing the overhead (ambient) light level. Occupancy sensors can also be incorporated into the system. |  | Konstantinos Papamichael, UC Davis & CLTC, 520-747-3834, kpapamichael@ucdavis.edu; Michael Myer, PNNL, michael.myer@pnl.gov
4 | Super T8 Lighting | Almost any fluorescent lighting system in most building types and settings. | Super T8 lamps are 32W T8 lamps but with a barrier-coat design, high lumen maintenance (88-92 percent end-of-life lumens), long service life and high light output—3100+ initial lumens as opposed to 2850 for a standard T8. Combining Super T8 Lamps with low ballast factor ballasts (BF of ≤ 0.77) on a one-for-one replacement will save 15 to 20%. | Spectrally Enhanced Lighting should be considered as an alternative when considering Super T8s. Super T8 technology can be used as a based strategy in combination with other fluorescent lighting based measures such as Low Ambient / Task Lighting, delamping configurations and daylighting controls. | Michael Siminovitch, CLTC, 530-747-3835, mjsiminovitch@ucdavis.edu
8 | LED / Solid State Lighting - Interior | Rapidly improving technology currently most applicable for downlights, tracklights, task lighting, accenting, high ceiling and high cost maintenance areas. | Interior LED retrofits are currently viable for downlights, tracklighting, sconces, and task lighting both line and low voltage. Replacements for incandescent A-Lamps have also been improving rapidly. Replacements for fluorescent tube lighting may be viable for high cost maintenance areas. | Evaluate samples of LED products in their intended fixtures and applications to gauge their “fit”—not only physically within the fixture, but in terms of lighting quality and aesthetic requirements. Evaluate test data and verify that product performance is based on standardized photometric testing (i.e., IES Method LM-79-08) and not LED chip performance alone. Performance and life of LED replacement lamps is highly dependent on their design and thermal management, which includes the fixture in which they are installed. The product should be covered by a warranty or return policy in case the lamp does not perform as claimed. Examine ways to incorporate solid state lighting into lighting retrofit strategies such as Low Ambient / Task Lighting. | Michael Siminovitch, CLTC, 530-747-3835, mjsiminovitch@ucdavis.edu; Ed Barbour, Navigant Consulting, 202-973-2478, edward.barbour@navigantconsulting.com; Linda Sandahl, PNNL, linda.sandahl@pnl.gov Jeff McCullough, PNNL, jeff.mccullough@pnl.gov Eric Richman, PNNL, eric.richman@pnl.gov
9 | LED / Solid State Lighting - Exterior | Street lighting, parking lots, garages, walk ways, building exteriors, landscape areas places where security and visual performance is critical | LED lighting economics can work in high electric cost area with lot of hours of use. Pricing is continually decreasing. Provides quality, white even lighting with good color rendition. When combined with bi-level motion sensors to reduce light levels in parking areas, garages and walk ways, greater cost effective savings can be achieved. | LEDs have no re-strike issues and can be effectively switched with bi-level motion sensor controls. | Michael Siminovitch, CLTC, 530-747-3835, mjsiminovitch@ucdavis.edu, Linda Sandahl, PNNL, Linda.sandahl@pnl.gov; Ed Barbour, Navigant Consulting, 202-973-2478, edward.barbour@navigantconsulting.com Jeff McCullough, PNNL, jeff.mccullough@pnl.gov Eric Richman, PNNL, eric.richman@pnl.gov
13 | Integrated Daylighting Systems | Perimeter and interior spaces w/ daylight exposure via windows and skylighting | Add electronic dimmable fluorescent ballasts, photosensors, and occupancy sensors where appropriate. This can be combined with network components, workstation controls and building management options. Integrated controls will provide significant savings on applied systems. |  | Francis Rubinstein, LBNL, FMRubinstein@lbl.gov, (510) 486-4096; Konstantinos Papamichael, UC Davis & CLTC, 520-747-3834, kpapamichael@ucdavis.edu; Tracy Beeson, PNNL, tracy.beeson@pnl.gov
15 | Bi Level Garage / Parking Lot / Pedestrian Lighting |  | This technology uses fluorescent and LED lighting sources with bi-level motion sensors to reduce lighting levels when the parking area is not in use. This technology can also be applied to pathway lighting where appropriate. |  | Konstantinos Papamichael, UC Davis & CLTC, 520-747-3834, kpapamichael@ucdavis.edu
20 | Induction Lighting | Areas requiring continuous illumination where long lamp life provides significant premium because of difficult maintenance or liability concerns. | Induction lighting is essentially a fluorescent light without electrodes or filaments, the items that frequently cause other bulbs to burn out quickly. Induction lamps offer the potential for very long life—up to 100,000 hours—while providing good color quality at competitive efficiencies. | Applications with High Potential for Induction Lighting: * In hard-to-reach locations that make maintenance costs high, such as street lighting and tunnels, or in high ceilings where there is continuous operation, such as hotel rotundas * Cold environments, such as supermarket walk-in coolers and freezers * Where high-quality lighting is required or highly desirable * Where reliability is highly valued * Where high lumen output is required * In areas that require lamps to reach full illumination immediately. | Michael Siminovitch, CLTC, 530-747-3835, mjsiminovitch@ucdavis.edu; Paul Kistler, Techval, paul.kistler@navy.mil, 805-982-1387
21 | HID Electronic/Dimming Ballasts | Exterior / Security Lighting and facilities with High Bay areas. | Most of these lights, typically metal halide or high pressure sodium lamps, are currently driven by magnetic ballasts. Several manufacturers now offer electronic ballasts (EBs) for these lamps. EBs promise better efficiency, longer lamp life, and faster start-up and restrike. | Need to evaluated relative cost / benefit and application of the 3 major high bay technologies: HID Electronic, Fluorescent, and LED. | Michael Siminovitch, CLTC, 530-747-3835, mjsiminovitch@ucdavis.edu
26 | Bi Level Stairwell Lighting | Most multi-story buildings | These products use integral occupancy sensor motion detectors to monitor the stairwell. When occupancy is detected, the lights go to full level. When the space has been vacated after a programmed period of time, the fixture goes to a minimum level. | Good technology to implement concurrently with an overall building lighting improvement project. | Michael Siminovitch, CLTC, 530-747-3835, mjsiminovitch@ucdavis.edu
36 | Efficient High Bay Fluorescent Lighting | Facilities with High Bay areas. | These can include either T5 or T8 fluorescent lighting systems for high-bay applications currently using metal halide fixtures. Fluorescent fixtures offer better light distribution, better light maintenance over the life of the lamp, improved color quality and on-off control (re-strike time) with lower energy consumption. | Spectrally Enhanced Lighting can be used in in combination with these retrofits. Need to evaluated relative cost / benefit and application of the 3 major high bay technologies: HID Electronic, Fluorescent, and LED. | Michael Siminovitch, CLTC, 530-747-3835, mjsiminovitch@ucdavis.edu, Stan Walerczyk, 925-944-9481 Stan@lighting wizards.com
42 | High Bay LED | Facilities with High Bay areas. | LED light sources offer several potential benefits compared to metal halide or fluorescent: reduced energy consumption because of the ability to provide a more precise light distribution; longer operating life and lower maintenance requirements; less heat introduced into the space; and greater controllability for dimming and on/off control. The net result is an overall potential for life cycle savings despite the current high cost of the technology. Relevant to the cold storage application, LED performance improves in colder temperatures. | Need to evaluated relative cost / benefit and application of the 3 major high bay technologies: HID Electronic, Fluorescent, and LED. | Linda Sandahl, PNNL, linda.sandahl@pnl.gov; Jeff McCullough, PNNL, jeff.mccullough@pnl.gov; Eric Richman, PNNL, eric.richman@pnl.gov ; Stan Walerczyk, 925-944-9481 Stan@lighting wizards.com
46 | Airfield LED Lighting | Airports, Air Stations and Bases. | Good application for colored LED lights, since LED is monochromatic. Reduced maintenance costs dramatically improve economics over existing incandescent. | Determine FAA approval | Paul Kistler, Techval, paul.kistler@navy.mil, 805-982-1387
HVAC
3 | Condensing Boilers | Housing, Service, Office, R&D facilities, Schools, Hospitals | Commercial boilers that are high efficiency due to their design to extract heat from flue gas moisture | Condensing boilers are good when the water entering the boiler is cold enough. Many boilers for space heating have return water temperatures too high for the flue gas to condense. Many have an outdoor reset that raises the water temperature when the outdoor temperature is cold, i.e., when the most heating occurs. If boilers are used to heat domestic hot water , i.e., cold water from the city mains, then that would be a good application. Also, possibly, for radiant heating in floors or thermal displacement ventilation where lower temps can be used. In new installations, air handlers and coils can be sized to use cooler water – they just have to be bigger and therefore cost more. FEMP Procurement regulations require Federal agencies to purchase gas hot water supply boilers, with an efficiency of at least 94%, if they have inputs between 300,000 and 12,500,000 Btu/h, have at least 4,000 Btu/h per gallon of water stored, and are intended for heating potable water. Effectively this means it must be a condensing boiler. FEMP specifications for other boilers are in progress. | Steven Parker, PNNL, 509-375-6300, steven.parker@pnl.gov Jim Lutz, LBNL, JDLutz@lbl.gov
5 | Commercial Ground Source Heat Pumps | Housing, Service, Office, R&D facilities | A ground source heat pump with loops feeding multiple packaged heat pumps and having a single ground source water loop. Unit capacity is typically 1-10 tons and may be utilized in an array of multiple units to serve a large load. | DOE/FEMP has made great progress with this technology. Primary barriers deal with design criteria and installation infrastructure direct to reduce installation cost and increase effectiveness. | Xiaobing Liu, ORNL, 865-574-2593, xliu2@ornl.gov
7 | Duct Sealants | Most building categories | Aerosol sealant is injected into the duct work to seal leaks. Can save on heating, cooling and fan energy, depending on building. |  | Mark Modera, LBNL-UC Davis, 530-754-7671, MPModera@ucdavis.edu; Paul Kistler, Techval, 805-982-1387, paul.kistler@navy.mil
12 | Water Cooled Oil Free Magnetic Bearing Compressors | Housing, Service, Office, R&D facilities, Schools, Hospitals, Prisons | Magnetic bearing, oil free 60 to 80 ton chiller compressor (also 150 tons). Onboard VFD and micro processor. Also small, light, quiet, low startup draw. | Applicable, but not limited, to the following conditions: Year-round cooling requirements; Long run-time at partial load; chiller retrofits, compressor replacements. | Paul Kistler, Techval, 805-982-1387, paul.kistler@navy.mil
16 | Wrap Around Heat Pipes | Housing, Service, Office, R&D facilities, Schools, Hospitals | Where humidity control is critical the typical way to do it is to over cool the air to condense out the excess moisture. Air is then too cold to supply to the space so the air must be reheated. Wrap around heat pipes wrap around the cooling coil to pre-cool the outside air before it hits the cooling coil allowing the cooling coil to do more work condensing out moisture. The heat pipe then re-heats the air on the backside of the cooling coil so it doesn’t have to be re-heated with strip heaters or some other means. | Most cost effective in humid climates. | Andy Walker, NREL, 303-384-7531, AndyWalker@NREL.gov
18 | Commercial Energy Recovery Ventilation Systems (ERV) | Site dependent on climate conditions, relative duct locations | ERV systems exchange heat between the outgoing exhaust air and the ventilation air being brought in. This allows reducing the capacity of the HVAC system and saves energy. Heat and energy recovery wheels are the most common. Other types include: energy recovery loops, heat pipes, plate exchangers. Some transfer both sensible and latent heat. | This has the greatest impact in climates where there is a large difference between indoor and outdoor temperatures for much of the year. The pressure drop across the ERV increases the power requirements of the blower. Therefore, in milder climates a bypass and a variable speed blower should be used to bypass the ERV when energy savings from the ERV are smaller than the increased blower power. “The federal government mandates energy recovery ventilation systems in federal buildings and recommends that schools and small businesses consider the use of energy recovery ventilation” (ACEEE)– US GSA, Facilities Standards for the Public Building Service, March 2005 (ACEEE)
19 | Air-side Economizers and Filters for Data Centers | Larger data centers (with raised floors and multiple rack aisles). | Install 100% outside-air cooling capability in a data center to provide free cooling. | May require larger ductwork. Very large savings are possible depending on the climate. | Otto VanGeet, NREL, 303-384-7369, Otto.VanGeet@nrel.gov Geoffrey Bell, Lawrence Berkeley National Laboratory, GCBell@lbl.gov, 510-486-7989
22 | HVAC Occupancy Sensors | Housing, Service, Office, R&D facilities, Schools, Hospitals, Prisons | Uses an occupancy sensor to detect when people are in spaces. When no one is in the room, controls reduce the thermostat set point in the winter and raise it in the summer. | A CO2 or occupancy sensor is linked to the HVAC system. The technology is best for spaces where there is variable occupancy that cannot be predicted solely by time. Occupancy sensors provide quicker control response than CO2 sensors and are less costly. Occupancy sensors may cause too rapid cycling if located in a space where there is frequent entering and exiting of occupants. CO2 sensors can allow controls to adjust the number of people in a space if a VAV system is used. If the interior space of a building has internal heat loads such that it is cooling even when cold outside, raising the thermostat temperature would be a misapplication of this control technology. | Paul Kistler, Techval, paul.kistler@navy.mil, 805-982-1387; David Faulkner, LBNL, d_faulkner@lbl.gov
24 | Data Center Cooling System Air Distribution Optimization | Larger data centers (with raised floors and multiple rack aisles). | Implement appropriate air distribution controls to prevent the mixing and recirculation of data center air before it reaches the servers. This is done by confining the chilled air distribution to data center cold aisles. | Other rack mounted computer cooling methods, such as liquid cooled racks may also be considered. | Otto VanGeet, NREL, 303-384-7369, Otto.VanGeet@nrel.gov Geoffrey Bell, Lawrence Berkeley National Laboratory, GCBell@lbl.gov, 510-486-7989
27 | CO2 Demand Ventilation Control (DVC) | Conference rooms and other rooms with variable occupancy | A DVC system modulates the level of ventilation to a building based on the current occupancy of the building, saving energy while still maintaining proper IAQ. Carbon dioxide sensors are commonly used but a multiple-parameter approach using TVOC, PM, formaldehyde an RH levels can also be used.CO2 sensors control the outside air damper to reduce the amount of outside air that needs to be conditioned and supplied to the building when occupancy is low. Works especially well for conference rooms and auditoriums that are frequently low occupancy but must be designed to supply outside air volume for worst case scenario. | Works especially well for conference rooms and auditoriums that are frequently low occupancy but must be designed to supply outside air volume for worst case scenario. Studies have shown large errors in some CO2 sensor readings. Offered by all major HVAC equipment and control companies. | Chris Scruton, CA Energy Commission, 916-653-0948, cscruton@energy.state.ca.us; Michael Apte, LBNL, mgapte@lbl.gov; Paul Kistler, Techval, 805-982-1387, paul.kistler@navy.mil
28 | Thermal Displacement Ventilation | Hospitals, Offices, Schools, Auditoriums | Thermal displacement ventilation provides slightly cooled air into the space at relatively low velocity, either through a raised floor system or via wall diffusers near floor level. These are combined with a 100% outside air system and can also provide heating. | Performance is highly dependent on climate, building type, occupancy characteristics and system design. Has been effectively used in schools.
29 | Demand Control Ventilation for Commercial Kitchen Hoods | Hospitals, Schools, Prisons, Housing, Service, and other facilities with large kitchen facilities | A demand control ventilation system (DCV) is an energy management system for commercial kitchen hoods. It optimizes energy efficiency by reducing the exhaust and MUA fan speed. This is accomplished by leveraging sensors to determine the minimum amount of exhaust air required to capture and contain effluent from the cook line. | Overall building air balance must be maintained. Saving are due to a reduction in blower energy but also potential savings from reduced heating or cooling. | Don Fisher, Food Service Technology Center (FSTC), 925-866-5770, dfisher@fishnick.com
30 | Active Chilled Beam Cooling with Dedicated OSA Ventilation | Buildings over 60,000 sf. | In a "chilled beam" system chiller energy is delivered efficiently to the zone by being carried in water. Air in occupied spaces is passed across the radiant chilled beam. Warmer water is used than in a VAV system, which helps reduces energy consumption. Small amounts of outdoor air are entrained into the larger supply of recirculated air to provide required ratio of fresh air. | Should be considered during new construction or major renovation only.
32 | Multi-Stage Indirect Evaporative Cooling | Offices, R&D, Service, Schools | An advanced evaporative cooler that can lower air temperatures without adding moisture. These systems evaporate water in a secondary (or working) airstream, which is discharged in multiple stages. No water or humidity is added to the primary (or product) airstream in the process. | Works best in a dry climate. Applicable to the Western USA. Well suited where high percentage of outside (ventilation) air is used or required. Hybrid versions of multi-stage indirect evaporative coolers that also include a DX coil have been developed to meet a wider range of cooling requirements. | Robi Roichaud, NREL, 303-384-7553, Robi_Robichaud@NREL.gov
34 | Dehumidification Enhancements for Air Conditioning in Hot-Humid Climates | Most building categories | Incorporation of a Cromer cycle dehumidification feature on a packaged air conditioner in hot-humid climates. The Cromer cycle is a novel combination of a desiccant wheel and a vapor compression air conditioner. | Good for hot-humid climates. In dryer climates the increase in fan power needed due to the desiccant wheel, may offset any cooling energy savings. | Charles Cromer, charlie@fsec.ucf.edu ; Douglas Kosar, GTI, 847-768-0725, duglas.kosar@gastechnology.org; Eric Kozubal, NREL, Eric.Kozubal@nrel.gov
35 | Compressor Cycling Controller | Most building categories & refrigeration equipment | Add-on system compliments existing controls to maximize (optimize) compressor operation. Software dynamically analyzes compressor cycles, achieving an overall reduction in run time without causing over cycling. Energy efficiency gains are achieved without affecting cooling capacity |  | Van D. Baxter, ORNL, 423-574-2104, baxterVD@ornl.gov
37 | Advanced Rooftop Packaged AC | Most building categories | Roof top AC with features that can improve their efficiency. These include Improved fans, economizers, diagnostics. Roof top units that have (a) condensing units that drain to the interior of a building, (b) better insulation, (3) duct dampers that prevent off-cycle losses due to convection loops that loose heat from the building. In addition, a roof top unit with a modulating compressor will be more efficient and have better humidity control (if the indoor blower or air handler is also variable speed). | Manufacturer installed economizers are recommended. Economizers have been known to fail in the past. Efficiency ratings do not take into account all of the benefits of these advanced features. Economizers should be commissioned. | Mark Modera, Western Cooling Efficiency Center, 530-754-7671, mpmodera@ucdavis.edu ; Jonathan Woolley, Western Cooling Efficiency Center - UC Davis, 530-752-1101, jmwoolley@ucdavis.edu; Vernon Smith, Architectural Energy, 303-444-4149, vsmith@archenergy.com
38 | Liquid Desiccant Air Conditioner | Hospitals, Offices, Prisons, Schools, Service | A liquid desiccant air conditioner (LDAC) deeply dries air using natural gas, solar energy, waste heat, bio-fuel or other fossil fuel to drive the system. By providing mostly latent cooling, the LDAC controls indoor humidity without overcooling and reheating. This unit is supplemented by an electric chiller or DX air conditioner that sensibly cools the building's recirculation air. The liquid desiccant is a concentrated salt solution that directly absorbs moisture. Most attractive in humid climates. | The need for very dry air and the availability of waste heat to regenerate the liquid desiccant are good applications for this technology. Some corrosion issues need to be addressed. | Eric Kozubal, NREL, Eric.Kozubal@nrel.gov; Douglas Kosar, GTI, 847-768-0725, douglas.kosar@gastechnology.org , dkosar@uic.edu, 312-413-2646;
40 | Thermal Destratifiers | Storage, Industrial, Other, Service | Small turbine like fans are mounted near the ceiling in high bay buildings such as hangars and warehouses to move warm air down to the occupant level in the heating season resulting in using less energy to heat the building. Needs to be installed in well insulated high bay buildings. | May want to consider radiant heating as an alternative. | Paul Kistler, Techval, paul.kistler@navy.mil, 805-982-1387
43 | Off-peak Precooling | Most building categories | Air conditioning and associated ventilation accounts for almost half of peak electric demand of commercial buildings so using off-peak electricity to provide a significant portion of space cooling can achieve considerable electricity cost savings. | Requires optimized control strategies that are site specific. Highly depending on differential of on-peak and off-peak electric rates. | ORNL
44 | Evaporative Precooling Systems | Most building categories | Evaporative Precooling System installs ahead of the condenser to lower the condenser pressure. These systems can also work with an economizer. Overall evaporative precooling reduces the requirement for energy intensive DX cooling. | Water usage needs to be taken into account. Applicable to dry climates. Several variations of this concept are available. | Moonis Ally, ORNL, 865-576-8003, allymr@ornl.gov
45 | Wireless Temperature Sensors | Most building categories | Wireless thermostats are connected into a building automation system (BAS). Ease of adding temperature sensors in more zones allows for greater spatial resolution of zone temperatures thereby providing confidence in control improvements through thermostat reset. In addition, ease of moving thermostats allows for a diagnostic capability in checking existing hard-wired thermostats.
Building Envelope
6 | High R-Value Windows | Most building categories | Highly insulating windows triple pane R5 or greater (U value 0.22 and lower) windows | R-5 windows available - DOE has a volume purchase program. The DOE research goal is an R-10 window. | Christian Kohler, LBNL, 510-486-5040, CJKohler@lbl.gov; Marc LaFrance, DOE, 202-586-4617, marc.lafrance@ee.doe.gov; Dariush Arasteh, LBNL, 510-486-8644, d_arasteh@lbl.gov; Graham Parker, PNNL, 509-375-3805
14 | Cool Roofs | Most building categories | Cool roofs—roofs that stay cool in the sun by minimizing solar absorption and maximizing thermal emission—lessen the flow of heat from the roof into the building, reducing the need for space cooling energy in conditioned buildings. Cool roofs may also increase the need for heating energy in cold climates. For a commercial building, the decrease in annual cooling load is typically much greater than the increase in annual heating load. | Climate issues can affect performance. More beneficial in warmer climates. Some heating energy increase in colder climates. Lower impact if the roof has more insulation. The Secretary of Energy directed all DOE offices to install cool roofs, whenever cost effective over the lifetime of the roof, when constructing new roofs or replacing old ones at DOE facilities. He also encouraged other federal agencies to do the same. | Ronnen Levinson, Lawrence Berkeley National Laboratory, (510) 486-7494, RMLevinson@lbl.gov
17 | Window films | Most building categories | A spectrally selective film used to decrease heat gained through a window | Window orientation is a factor in performance | Christian Kohler, LBNL, 510-486-5040, CJKohler@lbl.gov
33 | Colored Paint for Heat Reflective or Absorbtive Applications | Most building categories | New technology allows for paint to be any color in the visible spectrum, yet have either absorptive or reflective properties in the heat spectrum. | A typical application would be to reduce the heat load on a wall receiving significant solar insolation. | Ronnen Levinson, Lawrence Berkeley National Laboratory, (510) 486-7494, RMLevinson@lbl.gov
47 | Green Roofs | Most building categories with higher roof to conditioned floor area ratios. | Vegetation on the roof reduces heat load and adds insulation to the roof. Reduces storm runoff from roof. | Climate issues can affect performance. Greater weight loading on the roof. | Chris Hendrickson, Carnegie Mellon Univ., cth@cmu.edu; Robert Berghage, Penn State Univ., Horticulture, 814-863-2190, rdb4@psu.edu
48 | Aerogel Insulation - Piping, Ducts, and Buildings | Most building categories | Aerogel products displace current insulation material. As the thermal conductivity of the aerogels is so low, aerogel insulation tends to be far thinner than current insulation. | Higher price than other insulations. Special applications such as translucent wall panels. | Jan Kosny, Fraunhofer-MIT Center for Sustainable Energy Systems, 617-575-7250, jkosny@fraunhofer.org
49 | Smart Windows | Most building categories | Electrochromic glass uses electrical energy to transition between clear and darkened states. Darkened glass transmits less light and reduces heat gain when darkened, especially in dual pane windows. | Window orientation a factor in performance | Eleanor Lee, Lawrence Berkeley National Laboratory, ESLee@lbl.gov, 510-486-4997 (confirm)
50 | Phase Change Insulation | Most building categories | Insulation or drywall that contains phase change material and therefore has a similar effect as increasing thermal mass. | Applicable if temperature swings occur around the melting point of the phase change material. More economically viable concurrent with renovation projects. May be more applicable where peak load shedding is important. | Jan Kosny, Fraunhofer-MIT Center for Sustainable Energy Systems, 617-575-7250, jkosny@fraunhofer.org
Water Heating
11 | Condensing Water Heaters - Gas | Most building categories with residential size water heaters | Gas water heater that condenses water out of the flue gas to achieve higher efficiencies | FEMP Procurement regulations require Federal agencies to purchase storage water heaters with an efficiency of 94% or greater when they have an input of 75,000 Btu/h or greater. Effectively this means it must be a condensing water heater. | Jim Lutz, LBNL, 510-486-7302, JDLutz@lbl.gov Steven Parker, PNNL, 509-375-6300, steven.parker@pnl.gov
25 | Tankless Water Heater - Gas | Most building categories with residential size water heaters | Water heater that does not have a storage tank. Sold in condensing and non-condensing. A conventional non-condensing storage tank water heater has an EF of 0.60 and a typical non-condensing tankless water heater has an EF of 0.80. Efficiencies are dependent on the frequency of water draws for tankless WHs and total hot water consumption for tank type WHs. | A new type of hybrid tankless water heater includes a small buffer tank that mitigates some issues with a delay in hot water during the water heater purge cycle at the start of every draw. Gas tankless water heaters require a minimum flow as high as 0.7 gpm. If your draw is at a lower flow rate - the water heater will not fire. FEMP Procurement regulations require Federal agencies to purchase instantaneous (aka tankless) water heaters that have a thermal efficiency of 94% or greater, when they have an input of 200,000 Btu/h or greater. Effectively this means it must be a condensing water heater. | Jim Lutz, LBNL, 510-486-7302, JDLutz@lbl.gov
31 | Heat Pump Water Heater | Most building categories with residential size water heaters | Air to water heat pump to replace an electric resistance water heater. | Residential type ~ 50 gallon capacity or larger | Jim Lutz, LBNL, 510-486-7302, JDLutz@lbl.gov Van Baxter, ORNL, 865-574-2104, BaxterVDavid@ORNL.gov Steven Parker, PNNL, 509-375-6300, steven.parker@pnl.gov
39 | Solar Water Heating | Most building categories | Using solar thermal collectors to heat water for commercial building hot water | Site specific for collector placement. Best in regions with high insolation. Energy Independence and Security Act (EISA) of 2007 requires 30% of hot water demand in new Federal buildings and major renovations be met with SHW equipment provided it is life-cycle cost-effective. | Andy Walker, NREL, 303-384-7531, AndyWalker@NREL.gov; Danny Parker, FSEC; Bryan Russo, PNNL, bryan.russo@pnl.gov
Refrigeration
41 | Refrigeration Management System | Hospitals, Schools, Prisons, Housing, Service, and other facilities with large kitchen facilities | Refrigeration Management System for walk-in coolers and freezers | When refrigeration failures are identified, action must be taken to repair the system. | Paul Delaney, Southern California Edison, 626-812-7321, paul.delaney@sce.com Scott Mitchell, Southern California Edison, 626-815-7232, Scott.Mitchell@sce.com
Other
10 | PC Power Management | Most building categories with high PC populations | Network based software that manages the power consumption of computers by automatically putting them in stand-by or hibernate or other low energy consuming state without interfering with user productivity or IT functions. |  | Contact EPA contractor to schedule a technical assistance call. powermanagement@cadmusgroup.com
23 | Vending Machine Occupancy Sensor | Most building categories with high PC populations | Device detects when there are no personnel in the vicinity and powers down beverage vending machines. Does not completely turn off compressor, but reduces run times. | Controls having a similar impact may be an integral part of a new vending machine | Peter Biermayer, LBNL, PJBiermayer@lbl.gov 510-486-5983; Paul Kistler, Techval, 805-982-1387, paul.kistler@navy.mil

## Resources
FEMP - New Technologies - Resources
Rank | Technology | Manufacturers | Tech Brief | Publications: Case Studies, Assessments, Websites | [7 empty] | Tools / Calculators / Design Resources
Lighting
1 | Spectrally Enhanced Lighting | GE Lighting, Philips, Sylvania, others | DOE 2010 - Spectrally Enhanced Lighting: Port Hueneme Case Study | NAVFAC 2009 - TechVal slides - general technologies | DOE/EERE 2010 - Spectrally Enhanced Lighting: Business Office Case Study | DOE/EERE 2010 - Spectrally Enhanced Lighting: Sonoma State University Case Study | DOE/EERE 2010 - Spectrally Enhanced Lighting: Washington Navy Yard Case Study
2 | Low Ambient / Task Lighting | Numerous depending on fixtures used for task lighting. | Integrated Office Lighting System - CLTC | Integrated Office Lighting System - CLTC | PG&E/HMG 2009 - High Efficiency Office: Low Ambient/ Task Lighting Pilot Project - Small Office | NAVFAC 2009 - Navy Techval Program, FUPWG 2009 | High Efficiency Office: Low Ambient/ Task Lighting - Large Office | Bi Level Switching in Offices Spaces 2010 | Bi-level Switching in Office Spaces - CLTC
4 | Super T8 Lighting | GE Lighting, Philips, Sylvania |  | FEMMP 2010 - TechVal slides - general technologies | facilitiesnet.com 2004 - Lamps in a New Light
8 | LED / Solid State Lighting - Exterior | Luminaires-roadway & parking: SPILINGINGInc, VizorLED, Finelite Inc., GE Lighting Solutions |  | SMUD - Canopy Lighting | DOE 2010 - Solid State Lighting Gateway Demonstrations | FEMP/TechVal 2010 - LED Parking Lot Lighting | [5 empty] | DOE/FEMP 2010 - Exterior Lighting Guide | DOE/EERE 2010 - Caliper - fact sheet
9 | Airfield LED Lighting | LSI Industries, Invue Entri, Winona |  | FEMMP 2010 - TechVal slides - general technologies
13 | Integrated Daylighting Systems | Lutron, Easylite, Ledalite |  | ACEEE 2006 - Integrated Daylighting Systems (Dimming Ballasts) | CLTC 2010 - Self Commissioning Dual Loop Sensor Dimming Technology for Daylighting
15 | Bi Level Garage / Parking Lot / Pedestrian Lighting |  |  | CLTC 2010 - Bi level fluorescent parking garage luminaire | PG&E 2009- - Bi Level Parking Lot Lighting - PDF | CLTC 2010 - Bi level parking garage& parking lot - CEC | SMUD 2010 - Bi-level LED Lighting |  |  |  |  | DOE/FEMP 2010 - Exterior Lighting Guide
20 | LED / Solid State Lighting - Interior | Downlighting: Cree, Edison Price Lighting, Intense lighting; Industrial: Digital Lumens, LightWild, Albeo Technologies, Accent: Cooper lighting, Lighting Services Inc., Amerlux Global Lighitng Solutions, DaSal Industries, USAI; Cove Lighting: Tempo Industries Inc.; Wall washing & grazing: Visa Lighting, Finelite, Edison Price Lighting | DOE/EERE website | SMUD 2008 - LED Downlights | SMUD 2003 - General Info on LEDs | DOE/EERE - 2009 - LED Replacements for Incandescent Lamps | ASHRAE 2010 - SSL Technology | ASHRAE 2010 - SSL Applications | DOE/EERE 2010 - Solid-State Lighting - Savings-General | DOE/EERE 2008 - niche applications |  | DOE/EERE 2010 - Caliper - fact sheet
21 | HID Electronic/Dimming Ballasts | Lumetric, Advance / Philips, Dynamic Ballast Corp., ROM Light International, Metrolight, | FEMP 2010 - Dimming Controllers for Outdoor Lighting | SMUD CAT Tech Evaluation Report - HID Labs SmartPOD | Navy Techval Program, FUPWG 2009 | PG&E 2008 - HID Electronic Ballast - Stockton/Central Valley Area, CA | PG&E 2008 - HID Electronic Ballast - San Francisco Bay Area | CEC 2005 - Evaluations of Electronic Ballasts and Related Controls for HID Lighting Systems
26 | Bi Level Stairwell Lighting | LaMar Lighting Co. Blinky Inc. |  | CEC/PIER 2008 - Bi-level Smart Stairwell Lighting System | CLTC 2007 - Bi-level Smart Stairwell Luminaire - CLTC | PG&E 2005 - Stairwell Lighting Report - Fillmore Center, San Francisco | NYSERDA - Verizon Office Building Case Study
36 | Efficient High Bay Fluorescent Lighting |  |  | SMUD 2002 - T-5 High bay lighting | NRCAN - High bay lighting intro
42 | High Bay LED |  |  | webspace: FEMP Emerging Tech 2010 - see CPUC directory
46 | Induction Lighting | GE Lighting, Philips, Sylvania | DOE/EERE Blog 2009 - Induction Lighting: An Old Lighting Technology Made New Again | SDG&E 2010 - Advanced Street Lighting Technologies Assessment Project - City of San Diego | SMUD 2003 - Induction Lighting Systems | [6 empty] | Advanced Lighting Guideline - online | CLTC 2010 - Advanced Lighting Guide website
HVAC
3 | Condensing Boilers |  |  | CEE 2001 - Market Assessment for Condensing Boilers - CEE | ACEEE 2004 - Energy Saving Technologies | CEE 2001 - Commercial Gas Boilers - Condensing | Annual Efficiency Calculation for Condensing Boilers |  |  |  |  | FEMP 2010 - Procurement Spec - Hot Water Supply Boiler
5 | Commercial Ground Source Heat Pumps | At least 16 commercial and residential manufacturers were identified as operational in the U.S.A. - DOE study; http://www.geoexchange.org/find-a-pro/geothermal-heat-pump-directory.html | DOE - Geothermal Heat Pumps | ACEEE 2009 - Commercial Ground Source Heat Pumps - One Pipe Loops | FEMP/ORNL 2002 - Geothermal Heat Pump Program | FEMP 2003 - Geothermal Heat Pump feasibility | Energy Center of Wisconsin 2000 - Emissions and Economic Update of Geothermal Heat Pumps | FEMP/ORNL 2001 - How to Buy an Energy Efficient Ground-Source Heat Pump | ACEEE 2009 - Energy Savings HVAC Technologies | FEMP 2001 - Ground Source Heat Pumps Applied to Federal Facilities |  | GeoExchange Directory | List of Geothermal Companies | International Ground Source Heat Pump Association
7 | Duct Sealants | Aeroseal (Carrier) | ASHRAE 2003 - Improved Duct Sealing | SMUD - Aeroseal Duct Sealing Program | Aeroseal duct sealing - FAQ | NAHB - duct sealing | [5 empty] | Aeroseal Duct Sealing Calculator | Flex Your Power 2010 - Duct Sealing
12 | Water Cooled Oil Free Magnetic Bearing Compressors | Turbocor, OEMs: MCQuay International, Multistack LLC, Smardt Inc., Thermal Care |  | FEMP - Variable Speed Compressor TechVal Results | Danfoss - Turbocor Case Studies | Danfoss - Turbocor Home Page
16 | Wrap Around Heat Pipes | Heat Pipe Technology, Inc. www.heatpipe.com |  | Heat Pipe Technology, Inc. | Heat Pipe Technology Corp. #2 | Heat Pipe Technology - 1996 | TropicCool Engineering Corp. | Colmac Coil | Economic Assessment Report-UK | Carolina Heat Pipe
18 | Commercial Energy Recovery Ventilation Systems (ERV) | Airxchange, Renewaire ; http://industrialhvacresource.com/category/energy-recovery-ventilation.html |  | ACEEE 2009 - Emerging Energy-Savings HVAC Tech | ERV mfr web site -Renewaire | [6 empty] | School Advanced Ventilation Software
19 | Air-side Economizers and Filters for Data Centers |  |  | ETCC 2009 - Impact of Air Filtration on Energy and IAQ on Economizer Based Data Centers | Air side economizer issues addressed - LBNL | DOE - Best Practices Guide for Energy-Efficient Data Center Design
22 | HVAC Occupancy Sensors |  |  | Lighting Design Resources 2010 - website | DOE/FEMP/NAVFAC 2010 - Navy TechVal Slides
24 | Data Center Cooling System Air Distribution Optimization |  |  | DOE/FEMP 2010 - Best Practices Guide for Energy-Efficient Data Center Design | DOE - Data Center Air Management Presentation | FEMP - Data Center Efficiency website | LBNL 2010Alternative cooling for data centers | Data Center Organization website | ETCC 2007-Data Center Air Management Report |  |  | DOE - Data Center Efficiency Savings Calculator
27 | CO2 Demand Ventilation Control (DVC) | Offered by all major HVAC equipment and control companies. |  | ASHRAE 2009 - An Updated Look at DCV Approaches | FEMP 2004 - Federal Technology Alert - Demand Controlled Ventilation Using CO2 Sensors | United Technologies 2010 - Demand Control Ventilation | Automated Buildings.com 2010 - Smart Demand Ventilation Article | ASHRAE 2001 - Demand Control Ventilation Using CO2 | DOE 2006 - Review of Demand Control Ventilation | LBNL 2009 - Assessment of DCV in California |  | EPA - HVAC Systems Design Tools | School Advanced Ventilation Engineering Software
28 | Thermal Displacement Ventilation | Halton, AEC |  | CEC PIER 2002 - Thermal Ventilation in Schools | ACEEE 2004 - See underfloor ventilation ECM report | NIST 2005 - Initial Evaluation of Displacement Ventilation in the U.S. | [5 empty] | ASHRAE 1998 - Design Guidelines for Displacement Ventilation
29 | Demand Control Ventilation for Commercial Kitchen Hoods | Melink Corporation - Intelli-Hood, Halton Company, Captive Aire |  | ETCC/SCE 2009 - Demand Control Ventilation for Commercial Kitchen Hoods | SMUD 2008 - Demand Ventilation System - Technology Report | Food Service Technology Center - Demand Ventilation | Engineered Systems Mag. 2002 - Air Balance Fundamentals for the Modern Restaurant | Engineered Systems Mag. 2009 - Kitchen Exhaust Hoods
30 | Active Chilled Beam Cooling with Dedicated OSA Ventilation | SEMCO, Trox Technik, SAS International, Grada, Swegon, Dadanco USA, NuClimate Inc.. http://www.archiexpo.com/architecture-design-manufacturer/chilled-beam-3068.html | Buildings.com 2008 - Chilled Beam System | Active Chilled Beam Cooling with DOAS | ACEEE 2009 - Energy Saving HVAC Technologies | ASHRAE 2009 - Chilled Beams for Thermal Comfort | TROX - Chilled Beams 101 | FacilitiesNet 2007 - Article on Chilled Beams
32 | Multi-Stage Indirect Evaporative Cooling | Manufacturers: Idalex Technologies, Inc.; Spreakman CRS Product names: Coolerado Cooler; Oasys |  | FEMP 2007 - Technology Installation Review - Coolerado Cooler Helps to Save Cooling Energy and Dollars | SMUD 2010 - Coolerado | Coolerado 2009 - M-Cycle: Beyond Confort Cooling | Idalex - Maisotsenko Cycle - How-it-works
34 | Dehumidification Enhancements for Air Conditioning in Hot-Humid Climates | Trane CDQ; SEMCO, Kathabar and AIL Research are developing a system | ACEEE 2009 - A Robust Feature Set For Residential Air Conditioners | ACEEE 2009 - Dehumidification Enhancements for Air Conditioners in Hot Humid Climates | ASHRAE 2009 - Energy Efficient Dehumidification | ASHRAE 2006 - Dehumidification System Enhancements | TAMU 2001 - Cromer Cycle Air Conditioner | New Approach to Energy Saving for Rooftop AC | School Case Study-ORNL 2005 | ORNL - News Release | ACEEE 2009 - Emerging Energy Savings HVAC Technologies
35 | Compressor Cycling Controller | Smartcool Systems Inc. (don't know of any other manufacturers) |  | SmartCool home page | ORNL 2004 - Evaluation of Abbotly Technologies Compressor Control
37 | Advanced Rooftop Packaged AC | Carrier, Lennox, Aaon | DOE 2000 - Tech Fact Sheet | ACEEE 2009 - Emerging Energy-Savings HVAC Tech | ACEEE 2009 - Advanced (Commercial AC) Modulating HVAC Compressors | E Source 2010 - Roof Top AC Options | CEC - PIER - HVAC with fault detection and diagnostics | ACEEE 2009 - Advanced "Gas-Pack" Rooftop Packaged Air-Conditioner |  |  |  | http://www.pnl.gov/uac/
38 | Liquid Desiccant Air Conditioner | Kathabar, AIL Research, Inc., AEX, Inc., DuCool, DryKor, Ficom, L-DCS, Menerga | NREL - Liquid Desiccant | ACEEE 2009 Report - Liquid Desiccant | ASHRAE 2008 - Liquid Desiccant Air Conditioners | ACEEE 2009 - Emerging Energy-Savings HVAC Tech | ACHR2010 News article | Conde - LCAC overview report | Science Daily 2010 - NREL-liquid desiccant & evap AC combined
40 | Thermal Destratifiers | Avedon Engineering, Inc. |  | NFESC (Navy) - Evaluation of Thermal Destratifiers | Airius brand destratifier website
43 | Off-peak Precooling | more of a strategy then a product |  | ASHRAE 2009 - Using Off-Peak Pre-Cooling | LBNL/CEC 2006 - Demand shifting with thermal mass in large commercial buildings-LBNL5885
44 | Evaporative Precooling Systems | (1) Evaporcool / Green HVAC Solutions; (2) AMAX |  | SMUD 2010 - Technical Evaluation Report: Ev aporcool Precooling System | 2009 SCE - Performance Evaluation of Evaporatively Cooled Split System | AMAX (mfr.) web site
45 | Wireless Temperature Sensors | Inovonics Wireless Corp |  | FEMP 2007 Technology Installation Review - Wireless Temperature Sensors for Improved HVAC Control | Similar:Wireless for Controls: An Update, ASHRAE Journal, August 2008
Building Envelope
6 | High R-Value Windows |  | DOE - Energy Efficient Windows - DOE- Building Technology Program | Serious Windows website- for commercial applications | ACEEE 2006 - Zero Energy Windows | National Fenestration Rating Council website | Efficient Windows Portal |  |  |  |  | DOE 2010-Savings calculator for R-5 Windows and Low-e Storm Windows | DOE - Windows for high-performance buildings design tool | LBNL - Software list for windows and daylighting | DOE - R-5 Window Volume Purchase Program
14 | Cool Roofs | Cool Roof Rating Council Product Directory | DOE/FEMP- 2000- “How to Buy ‘Cool’ Roof Products” by FEMP | Energy Efficiency Journal 2009 - Potential benefits of cool roofs on commercial buildings | DOE/FEMP 2010- Guidelines for Selecting Cool Roofs | DOE/FEMP 2010-Cool Roof Resource Guide for Federal Agencies | Energy Star2010 - Cool Roof Products | CEC-LBNL-ORNL-2008 - Cool Colors Project-pub list |  |  |  | ORNL/LBNL Roof Savings Calculator- v 0.9 | DOE/ORNL Cool Roof Calculator (flat roofs) v1.2 | Cool Roofs Rating Council-product directory
17 | Window films |  |  | 2010-Smart Thermochromic Window Film Article | NAHB - Window films
33 | Colored Paint for Heat Reflective or Absorptive Applications | Coolwall | ORNL Report Summary | DOE/ORNL 2006 - Energy Savings for Stucco Walls Coated with Cool Colors | Eley 2003 - Supercore textured coating energy savings calculations | ORNL 2005 - presentation of field study results | Procote-heat reflective paint | Hy-Tech - Insulating Paint Additive | Insuladd - heat reflective paint additive
47 | Green Roofs |  |  | DOE/FEMP 2004 Green Roofs Technology Alert | EPA-2010- Green Roofs | American Society of Civil Engineers Technical Paper-2010 Cost effectiveness of green roofs | Case Study 2007- Target Green Roof Option | Penn State - Center for Green Roof Research | Green Roof Industry Portal-2010 | Journal 2008- Roof-envelope ratio on green roof energy performance | Journal 2008 - Green Roof comparisons
48 | Aerogel Insulation - Piping, Ducts, and Buildings | Aspen Aerogels | NAHB Tool Base Residential Green Roofs | ORNL-2006 - Aerogel Wall Technologies | NAHB Toolbase: Translucent Walls and Windows | Aspen Aerogel Insulation-product literature | Cabot - Aerogel for daylighting | Thermablock Aerogel Insulation | Kalwall Translucent Wall Panels |  |  | ORNL-2004 - Whole Wall R-Value Calculator
49 | Smart Windows |  | ASHRAE 2009-Technologies for Smart Windows | ACEEE-2006-Zero Energy Windows | CEC/PIER 2006 - Advancement of Electrochromic Windows | LBNL Publications | [5 empty] | Comfen 2010 - tool to evaluate fenestration alternative | DOE 2008- Facade Design Tool
50 | Phase Change Insulation | Microtek, Advanced Fiber Technology (AFT) |  | DOE 2009 - Dynamic Insulation Building Technologies Research | ORNL 2005 - PCM-Enhanced Cellulose Insulation | Green Building Advisor Website 2009 - Storing Heat in Walls
Hot Water Heating
11 | Condensing Water Heaters - Gas | Major water heater manufucturers and some smaller manufacturers |  | FSTC 2010 - Water Heating Design Guide Final | Energy Star -condensing water heaters | FEMP 1998 | [5 empty] | FEMP 2010 - Procurement Specifications
25 | Tankless Water Heater - Gas | All major water heater mfrs. |  | ASHRAE 2009 - Gas tankless water heater | FEMP 2010 - Procurement Specifications | Energy Star - Tankless Water Heater | California Energy Commission (CEC) 2010 - Tankless WH
31 | Heat Pump Water Heater | Major water heater manufacturers and some smaller manufacturers | DOE/EERE - Hot Water Heat Pump brief | Wescor 2010 - HPWH - design details | NEEP 2009 - Heat pump water heaters | PG&E 2010 - Assessment Projects on Heat Pump Water Heaters | WAPA 2008 - Residential Heat Pump Water Heaters | BPA 2010 - Considering Heat Pump Water Heaters for the Pacific Northwest | Energy Star Heat Pump Water Heaters
39 | Solar Water Heating | Harpiris (NREL), SunCashe (Sempra) | DOE/EERE - Solar Water Heating Brief | Energy Star - Solar | FEMP Solar Hot Water Resources & Technologies | NREL 2007 - Technical Potential of Solar Water Heating | FEMP Technology Alert - Parabolic Trough Solar Water Heating | PG&E 2010 - Solar Hot Water Heating Systems | DOE 2010 - Solar Water Heating | NREL 1996 -Solar Water Heating | ACEEE 2010 - Hot Water Systems Lab - Florida Solar Energy Center | VEIC - Solar Hot Water Basics
Refrigeration
41 | Refrigeration Management System | Mfr. National Resource Management; Brand: CoolTrol | SMUD - CoolTrol Refrigeration Management System | SCE 2009 - Evaluation of Internet Based Refrigeration Monitoring & Control | SMUD - Technology Brief - CoolTrol
Other
10 | PC Power Management |  |  | Dell Case Study - power and patch | [7 empty] | Energy Star - Computer Power Management Savings Calculator
23 | Vending Machine Occupancy Sensor | Vending Miser |  | Vendingmiser Web Site | FEMP Designated Product: Beverage Vending Machines | DOE 2009 - Energy Saving Potential for Commercial Building Appliances | [5 empty] | VendingMiser Energy Savings Calculator

## Ranking Criteria
FEMP - New Technologies - Ranking Criteria
Score Weighting | 50% |  | 30% |  | 20%
| Energy Savings Potential |  | Cost Effectiveness |  | Probability of Success1
| Percent of Total Federal Building Energy Use | Score | Simple Payback Period | Score | Avg. of Success Criteria | Score
| > 2.45 | 5 | ≤3 | 5 | 5 | 5
| 1.96 - 2.45 | 4 | 3.1 - 6.0 | 4 | 4 | 4
| 1.46 - 1.95 | 3 | 6.1 - 9.0 | 3 | 3 | 3
| 0.96 - 1.45 | 2 | 9.1 - 12.0 | 2 | 2 | 2
| 0.46 - 0.95 | 1 | >12.0 | 1 | 1 | 1
| 0 - 0.45 | up to 1
1 See "Probability of Success" table below
Weighted Score (Rank) | = 50% * Energy Savings Potential + 30% * Cost Effectiveness + 20% * Prob of Success * 20 2
|  |  | 2 | Constant multiplied to provide (1 - 100) overall Scoring Scale
Probability of Success
Criteria | Description |  |  |  |  | Scoring
Supply Chain Strength | Manufacturers, Distribution Channel, Service, Warranty |  |  |  |  | (1 - 5)
Knowledge Base | Case Studies, Design Guides, Independent Evaluations/Assessments |  |  |  |  | (1 - 5)
Implementation Difficulty / Risk | Ease of Retrofit, Disruption to Occupants, Degree of Maintenance |  |  |  |  | (1 - 5)
Customer Acceptance | High Benefit/Cost ratio, Meeting Energy Goals, Improving facility, Low Potential for complaints, History of Success |  |  |  |  | (1 - 5)