## Sheet1
PROJECT INFORMATION
Property Address
System Brief Description
Size of systems (in tons)
Type of ground loop (e.g., horizontal)
Estimated annual kWh electricty saved
System Design Company
Installer Company (if different than designer)
Inspector
Inspection Date
Performance Test completed by
Performance Test Date
Ambient Temperature
Inspection Checklist
Pre-Installation
Yes | No | N/A | General |  | Note
Design and Installation being completed by IGSHPA certified contractor
Ensure that system design drawings (mechnical, electrical, etc.) are complete
Confirm that system is compliant with applicable drilling, building, and electrical codes
Obtain proper permits
Ensure warranties (ground-source heat pump, ground loop, installation) are sufficient:
Ground Loop warranty (recommended 25 year 90%, 50 year 80% minimum)
Ground-Source Heat Pump warranty (recommended 20 year 90%, 25 year 80% minimum)
Installation warrantly (industry standard)
Installation
Yes | No | N/A | General |  | Note
All system components are new and match invoice(s)
Components are located to allow access and are adequately protected
Yes | No | N/A | Ground Loop |  | Note
Geothermal ground loop is installed per workorder
Ground Loop is installed according to manufacturer specification:
Slinky - trench is of proper depth for local soil and climate conditions, tubing is kink free, fastners and couplings are tight
Horizontal - trench is proper depth for local soil and climate conditions, tubing is attached to trench walls, tubing is kink free, fastners and couplings are tight
Pond- ground loop is at a proper depth for local climate conditions, tubing is kink free, fastners and couplings are tight; the ground loop is properly weighted so it doesn't float
Vertical - well is sized and of sufficient depth for local soil and climate conditions, wellbore liner and/or tubing is installed, well head(s) is/are protected, fastners and couplings are tight, boreholes are grouted
Yes | No | N/A | Heat Pump/Mechanical |  | Note
Heat pump is installed per workorder
Changes to interior duct work are completed per workorder
Yes | No | N/A | Electrical |  | Note
Installation is consistent with electrical diagram.
GHP system (internal and external components) is grounded per Underwriters Laboratories ratings.
Fuses and breakers are sized and installed properly
Wire and conduit sizes installed per plan
GHP system is protected by a fuse or breaker.
Post-Installation
Yes | No | N/A | Visual Inspection Pior to Burial of Ground Loop |  | Note
Verify that physical installation of the entire sytems is per design drawing and manufacturer’s specification
Confirm that the ground loop is in good condition:
No loose of visibly damaged equipment
Tubing is clear of debris
Vertical system - well heads are protected
Horizontal system- tubing is properly attached to trench walls
Slinky system - tubing is no kinked
Pond system - location is well documented
Pressure test the ground loop
Confirm that wiring is completed (no loose connections or damaged wires)
Verify grounding of metallic surfaces that might become energized
Yes | No | N/A | Visual Inspection After Burial of Ground Loop |  | Note
Verify that the ground loop is properly buried and/or protected (except pond system)
Insure that ground surface is properly graded (except pond system)
Penetrations to building shell are sealed and fire resistance maintained.
Yes | No | N/A | Performance Testing |  | Note
Verify the system is performing within acceptable limits, as specified by designer and/or manufacturer
Yes | No | N/A | System Documentation |  | Note
All equipment and parts are labeled per program specifications
System has all required warning labels
All as-built equipment is properly documented
Copy of system diagram showing panels and meters
Emergency and maintenance contact information
Customer Manual is provided and includes:
Operation & Maintenance Instructions, with maintenance schedule
Electrical Design
Contractor Warranty
Manufacturers' Warranties
Permit(s)
Parts and Source List
Yes | No | N/A | Owner Education |  | Note
Owner understands basic system operation
Owner can verify if system is performing correctly
Owner understands required maintenance and schedule
Owner knows who to call in the case of repair
City inspection(s) have been passed: Permit #______________ Date____________