## Sheet1
PROJECT INFORMATION
Property Address
System Brief Descrition
Number of Panels
Orientation
Tilt
Estimated annual kBTU from SRCC rating
Solar Installer Company
Inspector
Inspection Date
Time of Measurement
Ambient Temperature
Solar Radiation (W/m2)
Water Temperature (°F)
Inspection Checklist
Yes | No | N/A | General | Note
Backup heater is either: ___electric ____natural gas ___propane
Installation is of industry standard and workmanlike quality.
Collectors are optimized for performance without sacrificing aesthetics.
Installation is consistent with plumbing diagram.
Installation is consistent with manufacturers’ instructions.
City inspection(s) have been passed: Permit #______________ Date____________
Yes | No | N/A | Materials | Note
Materials used outdoors are UV-resistant and listed for outdoor locations.
Materials are designed to withstand the temperatures to which they are exposed.
Dissimilar metals that have galvanic action are isolated.
Aluminum is not placed in direct contact with concrete.
High quality fasteners are used.
Structural members are made of approved materials.
Yes | No | N/A | Equipment and Installation | Note
All system components are new.
Solar collectors have OG-100 certification from the Solar Rating and Certification Corporation (SRCC).
System has SRCC OG-300 certification (if it serves a domestic water load in a single residence).
The system incorporates approved freeze and overheat protection methods that do not require customer action.
Any building insulation disturbed due to system installation is restored to previous condition.
Penetrations to building shell are sealed and fire resistance maintained.
Components, including solar storage and backup tanks, are located to allow access and are adequately protected.
Storage and backup tanks and related components are located in an enclosed tempered space.
Potable water supplied to the solar storage tank is believed to meet minimum quality standards.
Incoming potable pressure does not exceed 80 psi; pressure reducing valve (if required) is properly located.
If pressure reduction or back flow prevention on potable supply, expansion tank properly sized and installed.
If recirculation system exists, return piping is plumbed downstream of solar storage tank.
Yes | No | N/A | Collector Mounting | Note
Roof has 10 or more years useful life remaining (if roof-mounted).
Roof is capable of handling additional load (if roof-mounted).
Mounting is designed and installed to meet local codes.
Collectors are spaced a minimum of 1.5” off roof, or are properly flashed into roof.
All roof penetrations are flashed and sealed appropriately.
Mounting equipment is installed according to manufacturer specification.
Yes | No | N/A | Solar Access | Note
Solar resource is documented from location where shading is most significant.
Total Solar Resource Fraction (TSRF) is 75% or greater at all points on the collector(s).
Yes | No | N/A | Plumbing | Note
There are no leaks in the system plumbing.
Collector loop piping is copper or stainless steel. Potable water piping is copper, stainless steel, or PEX. Fittings are copper or brass. PEX connections are made with compression fittings.
Heat exchanger is copper, stainless steel, or cupronickel. Exception: HX is steel and meets additional requirements.
Potable plumbing in unheated overhead spaces is PEX with no connections
Piping runs are adequately and appropriately supported.
All pipes have minimum 3/4" high temperature rated elastomeric foam or factory-jacketed fibrous glass insulation. R-12 insulation on potable water piping in unheated spaces. Exception: 5/8” minimum for factory-insulated line sets.
Pipe insulation properly sized to fit pipe and continuously closed and sealed using a manufacturer-approved method.
Pipe insulation exposed to outdoors is adequately protected.
Underground piping is fully enclosed with appropriately-waterproofed R-6 insulation designed for underground use.
Underground potable piping is PEX with no buried connections. Underground collector loop piping is Type L copper.
Yes | No | N/A | Electrical | Note
Water heater and electrical supply are properly grounded.
Proper overload fuse or circuit breaker protection installed.
Wiring and connections comply with all applicable code.
Yes | No | N/A | Heat Transfer Fluid | Note
Heat transfer fluid (HTF) is appropriate for the system type and components used.
If used, antifreeze is inhibited propylene glycol (or approved glycerin) solution rated for usage up to 325 °F (163 °C). For system with single-wall heat exchanger, all HTF additives shall be FDA Generally Recognized as Safe.
If used, antifreeze solution is mixed to promote both heat transfer and freeze protection capabilities.
If antifreeze is not used, heat transfer fluid is distilled or deionized water with a suitable corrosion inhibitor.
If any additives are used, fill valve has a warning label: “Non-potable fluid. Do not drink.”
Yes | No | N/A | Backup Heater | Note
Solar water heating systems serves primary water heater(s).
Backup heater is electric/gas tank with minimum 40 gal energized storage or solar-compatible tankless gas heater.
Anti-convective piping with sweat fittings or brass unions installed at backup inlet and outlet.
All exposed hot pipes and first five feet of cold pipes are insulated.
If backup heater is new, meets program efficiency requirements and is fully compatible with solar input temperatures.
If backup heater is new or moved and installed over wood framed floor, drip pan installed and piped to drain.
If backup heater is new or moved and installed over concrete floor, R-10 pad bottom pad is installed.
Yes | No | N/A | Solar Storage Tank | Note
System has a minimum solar storage tank capacity of 1.25 gallons per square foot of net collector area.
Electric power shall not be connected to a roof-mounted tank or a separate solar storage tank.
If storage tank is installed over wood framed floor, drip pan installed and piped to drain.
If storage tank is installed over concrete floor, R-10 bottom pad is installed.
Anti-convective piping with sweat fittings or brass unions installed at storage tank’s cold water inlet.
If tank includes a sacrificial anode rod, means for changing the anode is provided.
Yes | No | N/A | Valves | Note
Fully ported isolation valves are installed, enabling bypass of solar system.
ASSE 1017 temperature actuated tempering valve installed downstream of backup heater and set to 140°F max.
If existing tankless heater is not rated for solar temp, tempering valve installed upstream of backup and labeled.
Check valves shall be installed on both hot and cold inlets to the tempering valve(s).
If hot water recirculation system, return water piped to both tempering valve inlets and aquastat controller installed.
Temperature & pressure relief valve installed on solar storage tank.
Valves installed for filling, flushing, and draining collector loop and potable water piping.
Yes | No | N/A | Passive Systems (if applicable) | Note
If solar tank is roof-mounted, system has adequate structural support per manufacturer's specifications.
If solar tank is roof-mounted, the potable water inlet and outlet piping shall be type L copper or brass piped to directly above the roof jack, where the connection to nonmetal piping is made.
Check valve is installed in the cold water supply line before the cold water expansion valve.
Thermometer is installed in piping between solar storage and backup heater near the top of the backup tank.
Temperature and pressure relief valve on solar tank is piped to drain.
If system uses glycol solution in a single wall heat exchanger, potable water supply pressure is 40 psi or greater.
Yes | No | N/A | Active Systems (if applicable) | Note
Collector loop plumbing was thoroughly flushed and pressure tested prior to charging with collector fluid.
Fluid has an adequate flow rate and circulates in proper direction.
Circulation pump is installed with shaft oriented horizontally.
System is designed to allow for isolation of the circulation pump.
Controller has correct settings and is mounted near solar tank and securely hard-wired or plugged into nearest outlet.
Sensors are placed correctly, attached securely, and adequately insulated. Plug sensor is installed on solar tank if a fitting is provided.
Sensor wiring has UV-rated exterior jacketing; is continuously attached and protected from abrasion, contact with 110V/220V lines/conduit, weather, and high temperature; and has solid connections.
Fill and drain valves have brass leak-proof caps.
Flow meter is installed on supply line to collector(s).
For systems with an external heat exchanger, a means of flow detection is installed in the potable water loop.
Thermometer is installed at hot water outlet port on solar storage tank.
Yes | No | N/A | System Documentation | Note
All valves, gauges and instruments are labeled per program specifications.
System has all required warning labels.
Maintenance Instructions sheet is mounted near/on system in clear plastic sleeve and includes: Emergency and maintenance contact information. Instructions for protecting system from overheating during summer vacations.
___Description and recommended frequency of homeowner maintenance.
___Copy of system diagram showing valves and meters.
___Emergency and maintenance contact information.
___Instructions for protecting system from overheating during summer vacations.
Customer Manual is provided and includes:
___Operation & Maintenance Instructions
___As-built Plumbing Diagram
___Mechanical Design
___Contractor Warranty
___Manufacturers' Warranties
___Permit(s)
___Parts and Source List
___Data Sheets for Pump, Valves, and Controller
Yes | No | N/A | Owner Education | Note
___Owner understands basic system operation.
___Owner can accurately read flow meter and thermometer.
___Owner understands required maintenance.
___Owner knows who to call in the case of an emergency.
___Owner understands proper start-up, shut-down and freeze protection procedure.